## Sheet1
Duct, Duct Insulation & Duct Jacketing Selection table
DG-2020 V5.0 Revision date: 08-19-2020
Item # | Duct service | Duct installation location | Duct joint sealer material | Duct material | Max. duct air leakage @ specified S.P. | Insulation type | Regulatory compliance | Jacket type or finished face type | Comments
1 | SA, RA, GEA, OSA & TA | Indoor exposed to unconditioned spaces. (e.g. mechanical rooms, tunnel entrances, etc.) | DuPont 1010, 1020 or approved equal | Galvanized steel, ASTM A653/A653M | 5% @ 4.0"w.c. for non-lab related areas and 1% @ 4.0" w.c. for lab related areas | 2.0" thick rigid glass fiber insulation board with aluminum ASJ foil faced backing, 3.0 lb./cubic foot density. Minimum R value of 8.0 | ASTM C612, ASTM C518, ASTM E 84, NFPA 90 A, NFPA 90B, CMC, CEC, SMACNA | Provide aluminum or PVC jacketing | Externally fasten FG boards to ductwork by means of mechanical pins and chemical adhesive as per manufacturer's recommendation. Provide water-proof tape at corners, breaks, joints and penetrations. The R value shall minimally meet the latest CMC, CEC, SMACNA and other applicable code requirements.
2 | SA, & RA | Indoor, above ceiling plenum in unconditioned space | DuPont 1010, 1020 or approved equal | Galvanized steel, ASTM A653/A653M |  | 2.0" thick fiberglass blanket wrap insulation with ASJ foil faced backing and moisture barrier, 0.75 lb./cubic foot density. Minimum R value of 6.3 | ASTM E84, ASTM C1290, ASTM C411, NFPA 90 A, NFPA 90B, CMC, CEC, SMACNA | jacketing is typically not required (see note #2 below) | Fibrous glass duct blanket wrap is applied to the exterior of sheet metal ducts by cutting to correct stretch-out length with a staple flap. The longitudinal seam is secured with staple or tape tab and, where a vapor retarder is required, sealed with pressure sensitive tape or glass fabric and mastic. Circumferential joints between pieces of duct wrap are sealed in the same manner. The R value shall minimally meet the latest CMC, CEC, SMACNA and other applicable code requirements.
3 | SA & RA | internal shafts, unconditioned not exposed to rain, moisture or elements |  | Galvanized steel, ASTM A653/A653M |  | 2.0" thick fiberglass blanket wrap insulation with ASJ foil faced backing and moisture barrier, 0.75 lb./cubic foot density. Minimum R value of 6.3 |  | jacketing is not required (see note #2 below)
4 | SA & RA | internal shafts, unconditioned not exposed to rain, moisture or elements |  | Galvanized steel, ASTM A653/A653M | 5% @ 4.0"w.c. for non-lab related areas and 1% @ 4.0" w.c. for lab related areas | 2.0" or thicker fiberglass blanket wrap insulation with aluminum ASJ foil faced backing and moisture barrier, 0.75 lb./cubic foot density. Minimum R value of 8.0 |  | jacketing is not required (see note #2 below)
5 | SA, RA & TA | Outdoors or on Roof and exposed to rain and other elements | SEKAFLEX 1A | Galvanized steel, ASTM A653/A653M |  | Minimum 3" thick spay-on foam | N/A | Granular coating with white finish | Refer to CIT's design guideline for application details and material specification. The R value shall minimally meet the latest CMC, CEC, SMACNA and other applicable code requirements.
6 | SA | Round, Rectangular and Square ducts, Indoor, exposed to view in conditioned space, | DOW-CORNING clear silicone sealant, model # 730 or GE-SCS 1201 | Galvanized steel, ASTM A653/A653M |  | 1.0" thick closed cell elastomeric foam. Similar to AP Armaflex internal lining (option #1) | ASTM E 84 | jacketing is not required (see note #2 below) | Insulation shall be attached to the interior of the duct by means of both mechanical fasteners and chemical adhesive. The R value shall minimally meet the latest CMC, CEC, SMACNA and other applicable code requirements.
7 | SA | Rectangular and Square ducts, Indoor, exposed to view in conditioned space | DuPont 1010, 1020 or approved equal | Galvanized steel, ASTM A653/A653M | 5% @ 4.0"w.c. for non-lab related areas and 1% @ 4.0" w.c. for lab related areas | 1.5" thick rigid glass fiber board with aluminum ASJ foil backing. (option #2). Minimum R value of 4.2 | ASTM E 84, ASTM C612, ASTM C518, NFPA 90 A, NFPA 90B, CMC, CEC, SMACNA | Provide aluminum or PVC jacketing | 1) The R value shall minimally meet the latest CMC, CEC, SMACNA and other applicable code requirements. 2) Follow NAIMA's installation instructions 3) Externally fasten FG boards to ductwork by means of mechanical pins and chemical adhesive as per manufacturer's recommendation.
8 | SA | Round spiral ducts, Indoor, exposed to view in conditioned space | DuPont 1010, 1020 or approved equal | Galvanized steel, ASTM A653/A653M |  | 1.5" thick fiberglass blanket wrap insulation with ASJ aluminum face backing, 0.75 lb./cubic foot density. Minimum R value of 6.3 | ASTM E84, ASTM C1290, ASTM C411, NFPA 90 A, NFPA 90B, CMC, CEC, SMACNA | cover the insulation with PVC or Aluminum jacketing | Fibrous glass duct blanket wrap is applied to the exterior of sheet metal ducts by cutting to correct stretch-out length with a staple flap. The longitudinal seam is secured with staple or tape tab and, where a vapor retarder is required, sealed with pressure sensitive tape or glass fabric and mastic. Circumferential joints between pieces of duct wrap are sealed in the same manner. The R value shall minimally meet the latest CMC, CEC, SMACNA and other applicable code requirements.
9 | RA | Indoor, exposed to view in conditioned space | DOW-CORNING clear silicone sealant, model # 730 or GE-SCS 1201 | Galvanized steel, ASTM A653/A653M |  | none | N/A | jacketing is not required (see note #2 below)
10 | RA | Indoor, exposed to view in un-conditioned space | DOW-CORNING clear silicone sealant, model # 732 or GE-SCS 1201 | Galvanized steel, ASTM A653/A653M | 5% @ 4.0"w.c. for non-lab related areas and 1% @ 4.0" w.c. for lab related areas | 1.5" thick rigid glass fiber insulation board, 3.0 lb./cubic foot density. Minimum R value of 8.0 | ASTM C612, ASTM C518, ASTM E 84, NFPA 90 A, NFPA 90B, CMC, CEC, SMACNA | jacketing is not required (see note #2 below) | 1) The R value shall minimally meet the latest CMC, CEC, SMACNA and other applicable code requirements. 2) Follow NAIMA's installation instructions. 3) Externally fasten FG boards to ductwork by means of mechanical pins and chemical adhesive as per manufacturer's recommendation.
11 | SA, RA, OSA ,TA & GEA | Direct buried below grade | Blue silicone sealant as manufactured by AQC industries | HDPE |  | insulation is not needed due to thickness of the plastic / HDPE duct material and its inherent insulating properties | ASTM: E 84, D2000, D394, D624, D412, D1002, D2240, D3807, D2412-96 | jacketing is not required (see note #2 below) | Underground duct systems shall be HDPE polyethylene similar to AQC Industries. All joints and connections shall be clamp and gasket fastened in accordance with manufacturers recommendations to ensure an air and water tight system. All ducts and fittings shall be installed and backfilled according to manufacturers recommendations, using pea gravel, sand or the equivalent with proper compaction. The R value shall minimally meet the latest CMC, CEC, SMACNA and other applicable code requirements. Ductwork shall be provided with tracer metal for detection from grade level. Ductwork material shall be fire-retardant grade.
12 | EA serving chemical fume hoods | Direct buried below grade | DOW-CORNING clear silicone sealant, model # 730 | 316 L stainless steel painted with 2-part epoxy paint on the outside | 1% @ -6.0"w.c. | none | N/A | jacketing is not required (see note #2 below) | Duct to be encased in 1 sack slurry 12" all the way around the entire circumference.
13 | EA serving chemical fume hoods | Indoor, exposed to view in conditioned or un-conditioned space or outdoors exposed to the elements | DOW-CORNING clear silicone sealant, model # 730 | 316 L stainless steel | 1% @ -6.0"w.c. | none | N/A | jacketing is not required (see note #2 below) | Apply a 2" wide bead of silicone sealant in a clean and even manner. End product must be done in a workmanlike manner and look visually presentable.
13 | EA serving chemical fume hoods with highly corrosive chemicals similar to HF, etc. | Indoor, exposed to view in conditioned or un-conditioned space or outdoors exposed to the elements | DOW-CORNING clear silicone sealant, model # 730 | 316 L stainless steel internally coated with HALAR or FRP as an alternative material | 1% @ -6.0"w.c. | none | N/A | jacketing is not required (see note #2 below) | 1) ECTFE is marketed as Halar 2) All air-side components exposed to highly corrosive vapors shall be HALAR coated.
14 | SA & RA | Indoor, outdoors exposed to the elements, concealed & exposed to view in conditioned or un-conditioned spaces | DuPont 1010, 1020 or approved equal | Galvanized steel, ASTM A653/A653M | 5% @ -6.0"w.c. | Internally lined with 1.5" thick Johns Manville Linacoustic RC Fiber Glass duct liner. Insulation shall be attached to the interior of the duct by means of both mechanical fasteners and chemical adhesive | NAIMA, SMACNA, ASTM C1338, G21, G22, C1071, C411 & INDA IST80,.6,UL, NFPA, CA Title 24, ASHRAE 62, ICC | jacketing is not required (see note #2 below) | Encapsulated FG insulation duct liner shall be used only when recommended by an acoustical engineer and approved by Caltech Mechanical engineer in writing
1) Maximum flame spread index not to exceed 25 and maximum smoke developed index not to exceed 50. 2) When noted on OPR, plans or specification, Provide duct jacketing as called out by the Architect or Engineer.
3) Legend: SA=supply air, RA=return air, GEA=general exhaust air, EA=exhaust air, TA=transfer air and OSA=outside air, ASJ=all weather service jacket, FSK=foil scrim kraft, S.P.= Static pressure, 4) All materials in active air plenums shall be plenum rated.
`