## HVAC Hydronic Piping
Date: 08/19/2020 | [7 empty] | Outline Mechanical and HVAC Hydronic Piping requirements
Revision 07
No | Abbreviation | Service | Location | Pipe Material | Class /Compliance | Type | Joint | Fittings | Valves | Insulation Material | Insulation Sizes | Jacket | Background Color / Letter Color | Remarks | Special Handling | Pressure Testing / Chemically Cleaning and Passivation | Rod Size / Hangers Spacing
H1 | CHWS & CHWR / MCHWS&R | Chilled Water Supply & Return + medium temperature chilled water supply and return (42DF -65DF) | Direct Buried, Below Grade | Pipe 1" -10" Domestic (US Made) seamless carbon steel pipe (No ERW, longitudinal seam and imported piping are allowed.) | ASTM A53-S, Grade A or Grade B Or ASTM A106 Grade B Seamless | Pipe 1" to 10": Schedule 40 | Butt Welded AWS D1.1 | Standard weight carbon steel, butt weld ASTM B16.9. | 1) pipes up to 2": NIBCO T-585-70-66, pipes 2.5": Apollo series 77-140, pipes 3"- 5": NIBCO LD3122-3. Pipes 6" and above: NIBCO LD3122-5 lug style butterfly valves. 2) Isolation valves for direct-buried pipes shall be placed in an accessible & adjustable concrete valve box of suitable size to accommodate repair and replacement | 1) Minimum 2" thick Cellular FOAMGLASS insulation by Pittsburg corning with "PITWRAP" CW plus jacketing 2) Field or factory applied Polyisocyanurate Rigid Foam, ASTM C591, K = 0.17 at 75F; Min Service Temp: -297F; Max Service Temp: 300F; Max Moisture Absorption: 0.1 % by volume; Trymer 2000XP by Dow Plastics. | See insulation thickness table in the appendix section | 150 mil Polyethylene or PVC with fused joints to achieve a water impermeable joint. | N/A | THERE IS A STRONG PREFERENCE TO NOT HAVE ANY DIRECT-BURIED CHW, HHW & MCHW PIPES ON CALTECH CAMPUS. SAID PIPES ARE REQUIRED TO BE RUN IN UTILITY TUNNELS INSTEAD. HOWEVER, IF THIS ACCOMMODATION IS NOT PRACTICAL , SAID PIPES SHALL BE INSTALLED IN A PRE-ENGINEERED DOUBLE-WALL CONDUIT/CARRIER PIPE SYSTEM SIMILAR TO "Perma-Pipe, Rovanco or Thermacor". SEE ROWS H27 & H28 FOR ADDITIONAL DETAILS. ===== 1) Provide stem extensions on isolation ball valves serving insulated pipes to accommodate operation of the valve handle without crushing the insulation material. 2) Provide butterfly valves for pipes 3" and larger . 3) provide concrete valve boxes for al valves serving direct-buried pipes | 1) design engineer or contractor shall analyze the pipe work and make any necessary provisions for thermal expansion and contraction [e.g. bolster pads & pillows, expansion loops or pre-engineered pipe and conduit systems] 2) clean and Chemically Passivate carbon steel pipe. Provide provisions for expansion and contraction as necessary to compensate for long runs and high temperatures fluctuations | Steel and copper piping system shall be chemically cleaned and passivated for a minimum of 48 hours. Pressure test piping system with compressed air for a minimum of 24 hours at 150 psig. Record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. Neutralize the chemicals and flush the system immediately after cleaning is completed and discharge the chemicals in a code approved manner in compliance with CIT design guide. Refer to campus design guide document for the details of cleaning & passivation procedures and chemicals. =============1) Direct buried pipes are acceptable only with written approval from CIT project manager : Minimum 3 inch wide polyethylene detectable type marking tape. The tape shall be resistant to alkalis, acids and other destructive agents found in soil and impregnated with metal tape or wire so that it can be readily detected after burial by standard locating equipment. 1. Lamination bond of one (1) layer of Minimum 0.35 mils thick aluminum foil between two (2) layers of minimum 4.3 mils thick inert plastic film. 2. Minimum tensile strength: 63 LBS per 3 inch width. 3. Minimum elongation: 500 percent. 4. Provide continuous yellow with black letter printed message repeated every 16 to 36 inches warning of pipe buried below (e.g.: "CAUTION CHILLED WATER BELOW", "CAUTION HEATING HOT WATER BELOW", etc.). 2) Direct-buried piping system shall be engineered using computer simulation program to elimate pipe stresses due to expansion and contraction. Make all provisions necessary to accommodate expansion and contraction caused by temperature variations. (e.g. insulation pillows, bolster pads, thrust blocks, anchors, expansion loops, etc. 3) Submit calculation and results according to the model analyzed with respect to the maximum allowable stress ratios as defined per ASME B31.1 – Power Piping for various materials. Stress ratios shall not exceed 1.0 as per ASME B31.1 . | N/A
H2 | CHWS & CHWR / MCHWS&R | Chilled Water Supply & Return + medium temperature chilled water supply and return (42DF -65DF) | Direct Buried, Below Grade | Pipe 12" & above: Domestic (US Made) seamless carbon steel pipe (No ERW, longitudinal seam and imported piping are allowed.) | ASTM A53-S, Grade A or Grade B Or ASTM A106 Grade B Seamless | Pipe 12" & above: Standard weight | Butt Welded AWS D1.1 | Standard weight carbon steel, butt weld ASTM B16.9. |  |  | See insulation thickness table in the appendix section |  | N/A |  |  |  | N/A
H3 | CHWS & CHWR / MCHWS&R | Chilled Water Supply & Return + medium temperature chilled water supply and return (42DF -65DF) | Above Ground | Pipe up to 3": Domestic (US Made) seamless copper tubing (No ERW, longitudinal seam and imported piping are allowed.) | ASTM B88, Seamless | Type L, Hard drawn | 1) Braze with 15% silver content silfloss brazing alloy. 2) Provide FxF threaded unions and FxF threaded isolation valves. | 1) ANSI / ASME B16.22, Solder wrought copper. 2) Press fittings as manufactured by Viega Propress, Mueller Streamline PRS or Elkhart Apollo Press | pipes up to 2": NIBCO T-585-70-66, pipes 2.5": Apollo series 77-140, pipes 3"- 5": NIBCO LD3122-3. Pipes 6" and above: NIBCO LD3122-5 lug style butterfly valves. Raised full faced spiral wound gaskets and B16 studs and nuts. Isolation valves installed higher than 10' above finished floor shall have chain operated hand wheel. | 1) Non-plenum rated applications: Polyisocyanurate Rigid Foam, ASTM C591, K = 0.19 at 75F; Min Service Temp: -297F; Max Service Temp: 300F; Max Moisture Absorption: 0.2% by volume; Trymer 2000XP by Dow Plastics 2) Provide vapor retardant jacketing with self-sealing laps similar to Dow Saran 540 CX with 1% or less permeation. 3) Plenum rated applications: Closed-cell phenolic insulation similar to Trymer Supercel | See insulation thickness table in the appendix section | Exposed Indoors: ASJ + 30mil PVC / Outdoors: ASJ + 0.016" Aluminum | Green / White with arrows in the direction of flow | 1) Provide stem extensions on isolation ball valves serving insulated pipes to accommodate operation of the valve handle without crushing the insulation material. | No soft solder allowed except within 6" of threaded fittings and couplings. design engineer or contractor shall analyze the pipe work and make any necessary provisions for thermal expansion and contraction. |  | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H4 | CHWS & CHWR / MCHWS&R | Chilled Water Supply & Return + medium temperature chilled water supply and return (42DF -65DF) | Above Ground | Pipe 4" & above: Domestic (US made) Seamless Steel Pipe (No ERW, longitudinal seam and imported piping are allowed.) | ASTM A53-S, Grade A or Grade B Or ASTM A106 Grade B Seamless | Pipe 4" to 10": Schedule 40, Pipe 12" & above: Standard weight | Butt welded AWS D1.1 or flanged. For flanged fittings, use raised face flanges and metal wound gaskets. Mechanical joint couplings required at final connections to equipment to facilitate de-coupling and maintenance. | Standard weight carbon steel, butt weld ASTM B16.9. |  |  | See insulation thickness table in the appendix section | Exposed Indoors: ASJ + 30 mil PVC / Outdoors: ASJ + 0.016" Aluminum | Green / White with arrows in the direction of flow | 1) Provide stem extensions on isolation ball valves serving insulated pipes to accommodate operation of the valve handle without crushing the insulation material. | design engineer or contractor shall analyze the pipe work and make any necessary provisions for thermal expansion and contraction. |  | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H5 | HHWS & HHWR | Heating Hot Water Supply & Return | Direct Buried, Below Grade | Pipe 1" -10" Domestic (US Made) seamless carbon steel pipe (No ERW, longitudinal seam and imported piping are allowed.) | ASTM A53-S, Grade A or Grade B Or ASTM A106 Grade B Seamless | Pipe 1" to 10": Schedule 40 | Butt Welded AWS D1.1 | Standard weight carbon steel, butt weld ASTM B16.9. | pipes up to 2": NIBCO T-585-70-66, pipes 2.5": Apollo series 77-140, pipes 3"- 5": NIBCO LD3122-3. Pipes 6" and above: NIBCO LD3122-5 lug style butterfly valves. | 1) Minimum 2" thick Cellular FOAMGLASS insulation by Pittsburg corning with "PITWRAP" CW plus jacketing 2) Field or factory applied Polyisocyanurate Rigid Foam, ASTM C591, K = 0.17 at 75F; Min Service Temp: -297F; Max Service Temp: 300F; Max Moisture Absorption: 0.1 % by volume; Trymer 2000XP by Dow Plastics. 3) only pre-insulated pipes from the factory will be acceptable for direct-buried Heating Hot Water applications. | See insulation thickness table in the appendix section | 150 mil Polyethylene or PVC | Yellow / Black with arrows in the direction of flow | 1) Provide stem extensions on isolation ball valves serving insulated pipes to accommodate operation of the valve handle without crushing the insulation material. 2) Provide butterfly valves for pipes 3" and larger . 3) provide concrete valve boxes for al valves serving direct-buried pipes | 1) Provide provisions for expansion and contraction as necessary to compensate for long pipe runs and high temperatures fluctuations 2) clean and Chemically Passivate carbon steel pipe. 3) Provide provisions for expansion and contraction as necessary to compensate for long runs and high temperatures fluctuations |  | N/A
H6 | HHWS & HHWR | Heating Hot Water Supply & Return | Direct Buried, Below Grade | Pipe 12" & above: Domestic (US Made) seamless carbon steel pipe (No ERW, longitudinal seam and imported piping are allowed.) | ASTM A53-S, Grade A or Grade B Or ASTM A106 Grade B Seamless | Pipe 12" & above: Standard weight | Butt Welded AWS D1.1 | Standard weight carbon steel, butt weld ASTM B16.9. |  |  | See insulation thickness table in the appendix section | 150 mil Polyethylene or PVC | Yellow / Black with arrows in the direction of flow |  |  |  | N/A
H7 | HHWS & HHWR | Heating Hot Water Supply & Return | Above Ground | Pipe up to 3": Domestic (US Made) seamless copper tubing (No ERW, longitudinal seam and imported piping are allowed.) | ASTM B88, Seamless | Type L, Hard drawn | 1) Braze with 15% silver content silfloss brazing alloy. 2) Provide FxF threaded unions and FxF threaded isolation valves. | 1) ANSI / ASME B16.22, Solder wrought copper. 2) Press fittings as manufactured by Viega Propress, Mueller Streamline PRS or Elkhart Apollo Press | pipes up to 2": NIBCO T-585-70-66, pipes 2.5": Apollo series 77-140, pipes 3"- 5": NIBCO LD3122-3. Pipes 6" and above: NIBCO LD3122-5 lug style butterfly valves. Raised full faced spiral wound gaskets and B16 studs and nuts. Isolation valves installed higher than 10' above finished floor shall have chain operated hand wheel. Isolation valves installed higher than 10' above finished floor shall have chain operated hand wheel. | Pre-molded rigid Fiberglass, ASTM C547 Type 1 for pre-molded fiberglass insulation, K = 0.24 at 75F; Min Service Temp: -20F; Max Service Temp: 450F; Max Moisture Absorption: 0.2% by volume; Owens Corning, Certainteed or John Manville | See insulation thickness table in the appendix section | Exposed Indoors: ASJ + 30 mil PVC / Outdoors: ASJ + 0.016" Aluminum | Yellow / Black with arrows in the direction of flow | provide stem extensions on all ball valves serving insulated pipes to accommodate operation of the valve handle. design engineer or contractor shall analyze the pipe work and make any necessary provisions for thermal expansion and contraction. | No soft solder allowed except within 6" of threaded couplings. For pipe work installed below 8'-0" AFF where insulation is subject to damage, provide Calcium Silicate insulation in lieu of fiberglass. Provide provisions for expansion and contraction as necessary to compensate for long pipe runs and high temperatures fluctuations. | Steel and copper piping system shall be chemically cleaned and passivated for a minimum of 48 hours. Pressure test piping system with compressed air for a minimum of 24 hours at 150 psig. record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. Neutralize the chemicals and flush the system immediately after cleaning is completed and discharge the chemicals in a code . approved manner in compliance with CIT design guide. Refer to campus design guide document for the details of cleaning & passivation procedures and chemicals. | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H8 | HHWS & HHWR | Heating Hot Water Supply & Return | Above Ground | Pipe 4" & above: Domestic (US made) Seamless Steel Pipe (No ERW, longitudinal seam and imported piping are allowed.) | ASTM A53-S, Grade A or Grade B Or ASTM A106 Grade B Seamless | Pipe 4" to 10": Schedule 40, Pipe 12" & above: Standard weight | Butt welded AWS D1.1 or flanged. For flanged fittings, use raised face flanges and metal wound gaskets. Mechanical joint couplings required at final connections to equipment to facilitate de-coupling and maintenance. | Standard weight carbon steel, butt weld ASTM B16.9. |  | Pre-molded rigid Fiberglass, ASTM C547 Type 1 for pre-molded fiberglass insulation, K = 0.24 at 75F; Min Service Temp: -20F; Max Service Temp: 450F; Max Moisture Absorption: 0.2% by volume; Owens Corning, Certainteed or John Manville | See insulation thickness table in the appendix section | Exposed Indoors: ASJ + 30 mil PVC / Outdoors: ASJ + 0.016" Aluminum | Yellow / Black with arrows in the direction of flow | provide stem extensions on all ball valves serving insulated pipes to accommodate operation of the valve handle. design engineer or contractor shall analyze the pipe work and make any necessary provisions for thermal expansion and contraction. |  |  | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H9 | CD, OCD, V | Equipment Cold Drains, Overflows Condensate Drains, Air Vent Pipes do not need to be insulated. | Above Ground | Domestic (US Made) seamless copper tubing (No ERW, longitudinal seam and imported piping are allowed.) | ASTM B88, Seamless | Type L, Hard drawn | 1) Braze with 15% silver content silfloss brazing alloy. 2) Provide FxF threaded unions and FxF threaded isolation valves. 3) Press fittings as manufactured by Viega Propress, Mueller Streamline PRS or Elkhart Apollo Press | ANSI / ASME B16.22, Solder wrought copper | N/A | Elastomeric, ASTM C534 Type I, ASTM C177, K = 0.27 at 75F, Armaflex by Armstrong Industries. Vent pipes do not | See insulation thickness table in the appendix section | Exposed Indoors: ASJ + 30 mil PVC / Outdoors: ASJ + 0.016" Aluminum | Green / White with arrows in the direction of flow | Braze copper pipe joints and non-threaded fittings with 15% silfloss. Threaded fittings shall be soft-soldered using 95/5 lead -free solder. Care should be taken not to anneal the threads. Purge with Nitrogen gas during the brazing process to prevent formation of oxides. | No soft solder allowed except within 6" of threaded couplings. |  | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H10 | SV or RV | Steam vent & steam relief vent Piping | Above Ground | Pipe 4" & above: Domestic (US made) Seamless Steel Pipe (No ERW, longitudinal seam and imported piping are allowed.) | ASTM A53-S, Grade A or Grade B Or ASTM A106 Grade B Seamless | Pipe 4" to 10": Schedule 40, Pipe 12" & above: Standard weight | Butt welded AWS D1.1 or flanged. For flanged fittings, use raised face flanges and metal wound gaskets. Mechanical joint couplings required at final connections to equipment to facilitate de-coupling and maintenance. | Standard weight carbon steel, butt weld ASTM B16.9. | N/A | Pre-molded rigid Fiberglass, ASTM C547 Type 1 for pre-molded fiberglass insulation, K = 0.24 at 75F; Min Service Temp: -20F; Max Service Temp: 450F; Max Moisture Absorption: 0.2% by volume; Owens Corning, Certainteed or John Manville | See insulation thickness table in the appendix section | Exposed Indoors: ASJ + 30 mil PVC / Outdoors: ASJ + 0.016" Aluminum | Green / White with arrows in the direction of flow | Provide provisions for expansion and contraction as necessary to compensate for long pipe runs and high temperatures fluctuations | N/A |  | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H11 | HUW | Humidifier make-up water using Deionized water | Above Ground | Seamless stainless steel pipe/tubing, Grade 304L. (ERW or longitudinal seamed pipes are unacceptable) Domestic US made, German and Japanese are acceptable. | ASTM-A312 / ASME-SA312, Seamless | schedule 10S | Options 1. Gas Tungsten arc welding (GTAW) or Tungsten inert gas welding (TIG). Options 2. Swagelok tube fittings are also acceptable. | 1) Non-flanged Fittings: ASTM- A403 schedule 10 seamless stainless steel butt welded. 2) flanged fittings : ASTM-A182 Stainless steel 150# class flanges, raised faced spiral wound fittings with B16 studs and nuts | Option 1. 800# class threaded 304L stainless steel gate valve with threaded union Option 2. SWAGELOK ball valve rated for steam application. Make and model # to be approved by Caltech. | N/A | N/A | N/A | Green / White with arrows in the direction of flow | N/A | clean stainless piping. Passivation is not required. |  | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H12 | MUW | General equipment and heat exchanger make-up water | Above Ground | Domestic (US Made), seamless copper tubing (No ERW, longitudinal seam and imported piping are allowed.) | ASTM B88, Seamless | Type L, Hard drawn | 1) Braze with 15% silver content silfloss brazing alloy. 2) Provide FxF threaded unions and FxF threaded isolation valves. | 1) ANSI / ASME B16.22, Solder wrought copper. 2) Press fittings as manufactured by Viega Propress, Mueller Streamline PRS or Elkhart Apollo Press | pipes up to 2": NIBCO T-585-70-66, pipes 2.5": Apollo series 77-140, pipes 3"- 5": NIBCO LD3122-3. Pipes 6" and above: NIBCO LD3122-5 lug style butterfly valves. Raised full faced spiral wound gaskets and B16 studs and nuts. Isolation valves installed higher than 10' above finished floor shall have chain operated hand wheel. | N/A | N/A | N/A | Green / White with arrows in the direction of flow | Install backflow preventer, pressure regulator and pressure relief valve on all makeup water systems, as per detail in the design guide. Braze copper pipe joints and non-threaded fittings with 15% silfloss. Threaded fittings shall be soft-soldered using 95/5 lead -free solder. Care should be taken not to anneal the threads. Purge with Nitrogen gas during the brazing process to prevent formation of oxides. | No soft solder allowed except within 6" of threaded couplings. |  | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H13 | HUD | Humidifier Equipment Hot Drains | Above Ground | Domestic (US Made) seamless copper tubing (No ERW, longitudinal seam and imported piping are allowed.) | ASTM B88, Seamless | Type L, Hard drawn | Braze with 15% silver content silfloss brazing alloy. Provide threaded connections at unions and valves | ANSI / ASME B16.22, Solder wrought copper | pipes up to 2": NIBCO T-585-70-66, pipes 2.5": Apollo series 77-140. provide stem extensions on all ball valves serving insulated pipes to accommodate operation of the valve handle. | Rigid Fiberglass, ASTM C335, K = 0.24 at 75F; Min Service Temp: -20F; Max Service Temp: 450F; Max Moisture Absorption: 0.2% by volume; Owens Corning, Certainteed or John Manville | See insulation thickness table in the appendix section | Exposed Indoors: ASJ + 30 mil PVC / Outdoors: ASJ + 0.016" Aluminum | Yellow / Black with arrows in the direction of flow | Humidifier shall incorporate an automatic drain cooler with blow down cycle and thermostatically controlled mixing valve to cool down condensate drainage to 140F prior to discharge to an approved plumbing receptor. | Braze copper pipe joints and non-threaded fittings with 15% silfloss. Threaded fittings shall be soft-soldered using 95/5 lead -free solder. Care should be taken not to anneal the threads. Purge with Nitrogen gas during the brazing process to prevent formation of oxides.. Provide provisions for expansion and contraction as necessary to compensate for long pipe runs and high temperatures fluctuations | Gravity systems shall be hydrostatic tested for 4 hours up to 10' of head. Close openings in system and fill with water and use a Bristol Gauge to record any observed leakage. | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H14 | STM | 50 PSIG Campus main Steam distribution pipes and below 50 PSIG pressure inside the buildings | Above Ground | Pipe up to 2": Domestic (US Made) seamless steel pipe (No ERW, longitudinal seam and imported piping are allowed.) | ASTM A53-S, Grade A or Grade B Or ASTM A106 Grade B Seamless | Pipe up to 2": Schedule 40 | Shielded metal arc welding (SMAW), Butt welded AWS D1.1 or flanged. | 1) Non-flanged Fittings: Class 300# standard weight ANSI / ASTM A234 Malleable iron carbon steel butt welded . 2) Flanged fittings: ASTM A-105 carbon steel 150# class, raised full faced with spiral wound gasket & B16 studs and nuts | up to 2" pipe:800# class, 2.5" and above pipe: 150 # class rising stem gate valves. Make and model # to be approved by Caltech. Isolation valves installed higher than 10' above finished floor shall have chain operated hand wheel. | 1) Pre-molded rigid fiberglass ASTM-C547 type 1 for pre-insulated pipe. 2) Rigid Fiberglass, ASTM C335, K = 0.24 at 75F; Min Service Temp: -20F; Max Service Temp: 450F; Max Moisture Absorption: 0.2% by volume; Owens Corning, Certainteed or John Manville. 3) In areas where pipe insulation is susceptible to physical damage, insulate with Calcium Silicate, ASTM C533, ASTM C335, K = 0.38 at 75F; Min Service Temp: 100F; Max Service Temp: 1200F; Max Moisture Absorption: 0.2% by volume; Calsilite Manufacturing Corp only. | See insulation thickness table in the appendix section | Exposed Indoors: ASJ + 30 mil PVC / Outdoors: ASJ + 0.016" Aluminum | Yellow / Black with arrows in the direction of flow | Insulate valves & associated trim components with fiberglass clamshell, blanket or boxed insulation. Provide preformed clamshell for fittings & valves. Or Approved Equal | For pipe work installed below 8'-0" AFF where insulation is subject to damage, provide Calcium Silicate insulation in lieu of fiberglass. Provide provisions for expansion and contraction as necessary to compensate for long pipe runs and high temperatures fluctuations | Steel and copper piping system shall be chemically cleaned and passivated for a minimum of 48 hours. Pressure test piping system with compressed air for a minimum of 24 hours at 150 psig. record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. Neutralize the chemicals and flush the system immediately after cleaning is completed and discharge the chemicals in a code . approved manner in compliance with CIT design guide. Refer to campus design guide document for the details of cleaning & passivation procedures and chemicals. | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H15 | STM | 50 PSIG Campus main Steam distribution pipes and below 50 PSIG pressure inside the buildings | Above Ground | Pipe 2.5" & above: Domestic (US Made) seamless steel pipe (No ERW, longitudinal seam and imported piping are allowed.) | ASTM A106 Grade B Seamless | Pipe 2.5" to 10": Schedule 40, Pipe 12" & above: Standard weight | Shielded metal arc welding (SMAW), Butt welded AWS D1.1 or flanged. | 1) Non-flanged Fittings: Class 300# standard weight ANSI / ASTM A234 Malleable iron carbon steel butt welded . 2) Flanged fittings: ASTM A-105 carbon steel 150# class, raised full faced with spiral wound gasket & B16 studs and nuts |  |  | See insulation thickness table in the appendix section | Exposed Indoors: ASJ + 30 mil PVC / Outdoors: ASJ + 0.016" Aluminum | Yellow / Black with arrows in the direction of flow | Insulate valves & associated trim components with fiberglass clamshell, blanket or boxed insulation. Provide preformed clamshell for fittings & valves. Or Approved Equal. design engineer or contractor shall analyze the pipe work and make any necessary provisions for thermal expansion and contraction. |  | Steel and copper piping system shall be chemically cleaned and passivated for a minimum of 48 hours. Pressure test piping system with compressed air for a minimum of 24 hours at 150 psig. record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. Neutralize the chemicals and flush the system immediately after cleaning is completed and discharge the chemicals in a code . approved manner in compliance with CIT design guide. Refer to campus design guide document for the details of cleaning & passivation procedures and chemicals. | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H16 | SCR | Steam Condensate Piping | Above Ground | Pipe up to 2": Domestic (US Made) seamless steel pipe, black welded ends (No ERW, longitudinal seam and imported piping are allowed.) | ASTM A106 Grade B Seamless | Schedule 80 | Threaded or AWS D1.1 Welded | ANSI / ASTM B16.9, Malleable iron, 300 lb. |  | 1) Pre-molded rigid fiberglass ASTM-C547 type 1 for pre-insulated pipe. 2) Rigid Fiberglass, ASTM C335, K = 0.24 at 75F; Min Service Temp: -20F; Max Service Temp: 450F; Max Moisture Absorption: 0.2% by volume; Owens Corning, Certainteed or John Manville. 3) In areas where pipe insulation is susceptible to physical damage, insulate with Calcium Silicate, ASTM C533, ASTM C335, K = 0.38 at 75F; Min Service Temp: 100F; Max Service Temp: 1200F; Max Moisture Absorption: 0.2% by volume; Calsilite Manufacturing Corp only. | Title 24 complaint. Refer to 2013 nonresidential CEC manual, Table 4-15-Standards table 120.3-A Pipe Insulation Thickness | Exposed Indoors: ASJ + 30 mil PVC / Outdoors: ASJ + 0.016" Aluminum | Yellow / Black with arrows in the direction of flow | Insulate valves & associated trim components with fiberglass clamshell, blanket or boxed insulation. Provide preformed clamshell for fittings & valves. Or Approved Equal. design engineer or contractor shall analyze the pipe work and make any necessary provisions for thermal expansion and contraction. | For pipe work installed below 8'-0" AFF where insulation is subject to damage, provide Calcium Silicate insulation in lieu of fiberglass. Provide provisions for expansion and contraction as necessary to compensate for long pipe runs and high temperatures fluctuations |  | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H17 | SCR | Steam Condensate Piping | Above Ground | Pipe 2.5" & above: Domestic (US Made) seamless steel pipe, black welded ends (No ERW, longitudinal seam and imported piping are allowed.) | ASTM A106 Grade B Seamless | Schedule 80 | Butt welded AWS D1.1 or flanged. For flanged fittings, use raised face flanges and metal wound gaskets. Mechanical joint couplings required at final connections to equipment to facilitate de-coupling and maintenance. | Standard weight, carbon steel, butt weld, ASTM A234, Class 300. |  | 1) Pre-molded rigid fiberglass ASTM-C547 type 1 for pre-insulated pipe. 2) Rigid Fiberglass, ASTM C335, K = 0.24 at 75F; Min Service Temp: -20F; Max Service Temp: 450F; Max Moisture Absorption: 0.2% by volume; Owens Corning, Certainteed or John Manville. 3) In areas where pipe insulation is susceptible to physical damage, insulate with Calcium Silicate, ASTM C533, ASTM C335, K = 0.38 at 75F; Min Service Temp: 100F; Max Service Temp: 1200F; Max Moisture Absorption: 0.2% by volume; Calsilite Manufacturing Corp only. | See insulation thickness table in the appendix section | Exposed Indoors: ASJ + 30 mil PVC / Outdoors: ASJ + 0.016" Aluminum | Yellow / Black with arrows in the direction of flow | Insulate valves & associated trim components with fiberglass clamshell, blanket or boxed insulation. Provide preformed clamshell for fittings & valves. Or Approved Equal. design engineer or contractor shall analyze the pipe work and make any necessary provisions for thermal expansion and contraction. | For pipe work installed below 8'-0" AFF where insulation is subject to damage, provide Calcium Silicate insulation in lieu of fiberglass. Provide provisions for expansion and contraction as necessary to compensate for long pipe runs and high temperatures fluctuations | Steel and copper piping system shall be chemically cleaned and passivated for a minimum of 48 hours. Pressure test piping system with compressed air for a minimum of 24 hours at 150 psig. record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. Neutralize the chemicals and flush the system immediately after cleaning is completed and discharge the chemicals in a code . approved manner in compliance with CIT design guide. Refer to campus design guide document for the details of cleaning & passivation procedures and chemicals. | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H18 | SCD | Steam condensate drain from humidifiers | Above Ground | pipes up to 2": Domestic (US Made), seamless copper tubing (No ERW, longitudinal seam and imported piping are allowed.) | ASTM B88, Seamless | Type L, Hard drawn | Braze with 15% silver content silfloss brazing alloy. Provide threaded connections at unions and valves | ANSI / ASME B16.22, Solder wrought copper | pipes up to 2": NIBCO T-585-70-66 | 1) Pre-molded rigid fiberglass ASTM-C547 type 1 for pre-insulated pipe. 2)Rigid Fiberglass, ASTM C335, K = 0.24 at 75F; Min Service Temp: -20F; Max Service Temp: 450F; Max Moisture Absorption: 0.2% by volume; Owens Corning, Certainteed or John Manville | See insulation thickness table in the appendix section | Exposed Indoors: ASJ + 30 mil PVC / Outdoors: ASJ + 0.016" Aluminum | Yellow / Black with arrows in the direction of flow | Insulate valves & associated trim components with fiberglass clamshell, blanket or boxed insulation. Provide preformed clamshell for fittings & valves. Or Approved Equal. provide stem extensions on all ball valves serving insulated pipes to accommodate operation of the valve handle. | Braze copper pipe joints and non-threaded fittings with 15% silfloss. Threaded fittings shall be soft-soldered using 95/5 lead -free solder. Care should be taken not to anneal the threads. Purge with Nitrogen gas during the brazing process to prevent formation of oxides. Provide provisions for expansion and contraction as necessary to compensate for long pipe runs and high temperatures fluctuations | Steel and copper piping system shall be chemically cleaned and passivated for a minimum of 48 hours. Pressure test piping system with compressed air for a minimum of 24 hours at 150 psig. record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. Neutralize the chemicals and flush the system immediately after cleaning is completed and discharge the chemicals in a code . approved manner in compliance with CIT design guide. Refer to campus design guide document for the details of cleaning & passivation procedures and chemicals. | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H19 | CS & CSCR | Clean Steam & Clean Steam Condensate return Piping | Above Ground | Seamless stainless steel pipe/tubing, Grade 304L. ERW or longitudinal seamed pipes are unacceptable. | ASTM-A312 / ASME-SA312, Seamless | schedule 10S | Options 1. Gas Tungsten arc welding (GTAW) or Tungsten inert gas welding (TIG). Options 2. Swagelok tube fittings are also acceptable. | Seamless stainless, Grade 304L. ASTM-A312 / ASME-SA312 or ASTM-A403 socket welded | Option 1. 800# class threaded 304L stainless steel gate valve with threaded union.--- Option 2. SWAGELOK ball valve rated for steam application. Make and model # to be approved by Caltech. Isolation valves installed higher than 10' above finished floor shall have chain operated hand wheel. | 1) Pre-molded rigid fiberglass ASTM-C547 type 1 for pre-insulated pipe. 2) Rigid Fiberglass, ASTM C335, K = 0.24 at 75F; Min Service Temp: -20F; Max Service Temp: 450F; Max Moisture Absorption: 0.2% by volume; Owens Corning, Certainteed or John Manville. 3) In areas where pipe insulation is susceptible to physical damage, insulate with Calcium Silicate, ASTM C533, ASTM C335, K = 0.38 at 75F; Min Service Temp: 100F; Max Service Temp: 1200F; Max Moisture Absorption: 0.2% by volume; Calsilite Manufacturing Corp only. | See insulation thickness table in the appendix section | Exposed Indoors: ASJ + 30 mil PVC / Outdoors: ASJ + 0.016" Aluminum | Yellow / Black with arrows in the direction of flow |  | clean Stainless steel pipe. Passivation of stainless steel pipe for this utility is not required. Provide provisions for expansion and contraction as necessary to compensate for long runs and high temperatures fluctuations | Stainless steel piping system shall be chemically cleaned and flushed as necessary. Pressure test piping system with compressed air for a minimum of 24 hours at 150 psig. record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. Neutralize the chemicals and flush the system immediately after cleaning is completed and discharge the chemicals in a code . approved manner in compliance with CIT design guide. Refer to campus design guide document for the details of cleaning & passivation procedures and chemicals. | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H20 | STM | Campus Steam Piping mains | Inside utility Tunnels and areaways | Domestic (US Made), seamless carbon steel pipe, black welded ends (No ERW, longitudinal seam and imported piping are allowed.) | ASTM A106 Grade B Seamless | Pipe 2.5" to 10": Schedule 40, Pipe 12" & above: Standard weight | Shielded metal arc welding (SMAW) | 1) Non-flanged Fittings: Class 300# standard weight ANSI / ASTM A234 Malleable iron carbon steel butt welded . 2) Flanged fittings: ASTM A-105 carbon steel 150# class, raised full faced with spiral wound gasket & B16 studs and nuts | up to 2" pipe:800# class, 2.5" and above pipe: 150 # class rising stem gate valves, Make and model # to be approved by Caltech. Isolation valves installed higher than 10' above finished floor shall have chain operated hand wheel. | Calcium Silicate, ASTM C533, ASTM C335, K = 0.38 at 75F; Min Service Temp: 100F; Max Service Temp: 1200F; Max Moisture Absorption: 0.2% by volume; Calsilite Manufacturing Corp only | See insulation thickness table in the appendix section | 12 ounce / square yard heavy canvas and arabol jacketing + 2 coats of high gloss water-proof white paint | Yellow / Black with arrows in the direction of flow | Insulate valves & associated trim components with fiberglass clamshell, blanket or boxed insulation. Provide preformed clamshell for fittings & valves. Or Approved Equal. Install bellows type expansion joints to compensate for thermal expansion and contraction. | clean and Chemically Passivate carbon steel pipe. Provide provisions for expansion and contraction as necessary to compensate for long runs and high temperatures fluctuations | Steel piping system shall be chemically cleaned and passivated for a minimum of 48 hours. Pressure test piping system with compressed air for a minimum of 24 hours at 150 psig. record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. Neutralize the chemicals and flush the system immediately after cleaning is completed and discharge the chemicals in a code . approved manner in compliance with CIT design guide. Refer to campus design guide document for the details of cleaning & passivation procedures and chemicals. | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H21 | SCR option 1 | Steam Condensate Piping mains | Inside utility Tunnels and areaways | Seamless stainless steel pipe/tubing, Grade 304L. ERW or longitudinal seamed pipes are unacceptable. | ASTM-A312 / ASME-SA312, Seamless | schedule 10S | Gas Tungsten arc welding (GTAW) or Tungsten inert gas welding (TIG) | 1) Non-flanged Fittings: ASTM- A403 schedule 10 seamless stainless steel butt welded. 2) flanged fittings : ASTM-A182 Stainless steel 150# class flanges, raised faced spiral wound fittings with B16 studs and nuts | up to 2" pipe:800# class, 2.5" and above pipe: 150 # class rising stem gate valves, Make and model # to be approved by Caltech. Isolation valves installed higher than 10' above finished floor shall have chain operated hand wheel. | Calcium Silicate, ASTM C533, ASTM C335, K = 0.38 at 75F; Min Service Temp: 100F; Max Service Temp: 1200F; Max Moisture Absorption: 0.2% by volume; Calsilite Manufacturing Corp only. Eslin filament E-Class fibers is also acceptable. | See insulation thickness table in the appendix section | 12 ounce / square yard heavy canvas and arabol jacketing + 2 coats of high gloss water-proof white paint | Yellow / Black with arrows in the direction of flow | 1) Insulate valves & associated trim components with fiberglass clamshell, blanket or boxed insulation. 2) Provide preformed clamshell for fittings & valves. Or Approved Equal. 3) Make all provisions necessary to accommodate expansion and contraction caused by temperature variations. (e.g. insulation pillows, thrust blocks, anchors, expansion loops, etc. 3) Submit calculation and results according to the model analyzed with respect to the maximum allowable stresses defined per ASME B31.1 – Power Piping for various materials. | clean Stainless steel pipe. Passivation of stainless steel pipe for this utility is not required. Provide provisions for expansion and contraction as necessary to compensate for long runs and high temperatures fluctuations | Stainless steel piping system shall be chemically cleaned and flushed as necessary. Pressure test piping system with compressed air for a minimum of 24 hours at 150 psig. record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. Neutralize the chemicals and flush the system immediately after cleaning is completed and discharge the chemicals in a code . approved manner in compliance with CIT design guide. Refer to campus design guide document for the details of cleaning & passivation procedures and chemicals. | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H22 | SCR option 2 | Steam Condensate Piping mains | Inside utility Tunnels and areaways | Domestic (US Made), seamless carbon steel pipe, black welded ends (No ERW, longitudinal seam and imported piping are allowed.) | ASTM A106 Grade B Seamless | Schedule 80 | Shielded metal arc welding (SMAW) | 1) Non-flanged Fittings: Class 300# standard weight ANSI / ASTM A234 Malleable iron carbon steel butt welded . 2) Flanged fittings: ASTM A-105 carbon steel 150# class, raised full faced with spiral wound gasket & B16 studs and nuts | up to 2" pipe:800# class, 2.5" and above pipe: 150 # class rising stem gate valves. Make and model # to be approved by Caltech. Isolation valves installed higher than 10' above finished floor shall have chain operated hand wheel. | Calcium Silicate, ASTM C533, ASTM C335, K = 0.38 at 75F; Min Service Temp: 100F; Max Service Temp: 1200F; Max Moisture Absorption: 0.2% by volume; Calsilite Manufacturing Corp only. Eslin filament E-Class fibers is also acceptable. | See insulation thickness table in the appendix section | 12 ounce / square yard heavy canvas and arabol jacketing + 2 coats of high gloss water-proof white paint | Yellow / Black with arrows in the direction of flow |  | clean and Chemically Passivate carbon steel pipe. Provide provisions for expansion and contraction as necessary to compensate for long runs and high temperatures fluctuations | Steel and copper piping system shall be chemically cleaned and passivated for a minimum of 48 hours. Pressure test piping system with compressed air for a minimum of 24 hours at 150 psig. record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. Neutralize the chemicals and flush the system immediately after cleaning is completed and discharge the chemicals in a code . approved manner in compliance with CIT design guide. Refer to campus design guide document for the details of cleaning & passivation procedures and chemicals. | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H23 | CHWS & CHWR | Chilled Water Supply & Return mains | Inside utility Tunnels and areaways | Pipe up to 3": Domestic (US Made), seamless copper tubing (No ERW, longitudinal seam and imported piping are allowed.) | ASTM B88, Seamless | Type L, Hard drawn | 1) Braze with 15% silver content silfloss brazing alloy. 2) Provide FxF threaded unions and FxF threaded isolation valves. | 1) ANSI / ASME B16.22, Solder wrought copper. 2) Press fittings as manufactured by Viega Propress, Mueller Streamline PRS or Elkhart Apollo Press | pipes up to 2": NIBCO T-585-70-66, pipes 2.5": Apollo series 77-140, pipes 3"- 5": NIBCO LD3122-3. Pipes 6" and above: NIBCO LD3122-5 lug style butterfly valves. Raised full faced spiral wound gaskets and B16 studs and nuts. Isolation valves installed higher than 10' above finished floor shall have chain operated hand wheel. | Polyisocyanurate Rigid Foam, ASTM C591, K = 0.19 at 75F; Min Service Temp: -297F; Max Service Temp: 300F; Max Moisture Absorption: 0.2% by volume; Trymer 2000XP by Dow Plastics | See insulation thickness table in the appendix section | 1) 12 ounce / square yard heavy canvas and arabol jacketing + 2 coats of high gloss water-proof white paint 2) vapor retardant jacketing with self-sealing laps similar to Dow Saran 540 CX with 1% or less permeation. | Green / White with arrows in the direction of flow | Insulate valves & associated trim components with closed cell clamshell, blanket or boxed insulation. Provide preformed clamshell for fittings & valves. Or Approved Equal. provide stem extensions on all ball valves serving insulated pipes to accommodate operation of the valve handle. design engineer or contractor shall analyze the pipe work and make any necessary provisions for thermal expansion and contraction. | No soft solder allowed except within 6" of threaded fittings and couplings. design engineer or contractor shall analyze the pipe work and make any necessary provisions for thermal expansion and contraction. |  | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H24 | CHWS & CHWR | Chilled Water Supply & Return mains | Inside utility Tunnels and areaways | Pipe 4" & above: Domestic (US made) Seamless Steel Pipe (No ERW, longitudinal seam and imported piping are allowed.) | ASTM A53-S, Grade A or B | Pipe 4" to 10": Schedule 40, Pipe 12" & above: Standard weight | Butt welded AWS D1.1 or flanged. For flanged fittings, use raised face flanges and metal wound gaskets. Mechanical joint couplings allowed at final connections to equipment to facilitate maintenance. | Standard weight carbon steel, butt weld ASTM B16.9. |  | Polyisocyanurate Rigid Foam, ASTM C591, K = 0.19 at 75F; Min Service Temp: -297F; Max Service Temp: 300F; Max Moisture Absorption: 0.2% by volume; Trymer 2000XP by Dow Plastics | See insulation thickness table in the appendix section | 1) 12 ounce / square yard heavy canvas and arabol jacketing + 2 coats of high gloss water-proof white paint 2) vapor retardant jacketing with self-sealing laps similar to Dow Saran 540 CX with 1% or less permeation. | Green / White with arrows in the direction of flow | 1) Insulate valves & associated trim components with fiberglass clamshell, blanket or boxed insulation. 2) Provide preformed clamshell for fittings & valves. Or Approved Equal. 3) Make all provisions necessary to accommodate expansion and contraction caused by temperature variations. (e.g. insulation pillows, thrust blocks, anchors, expansion loops, etc. 3) Submit calculation and results according to the model analyzed with respect to the maximum allowable stresses defined per ASME B31.1 – Power Piping for various materials. | Design engineer or contractor shall analyze the pipe work and make any necessary provisions for thermal expansion and contraction. |  | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H25 | HHWS & HHWR | Heating Hot Water Supply & Return mains | Inside utility Tunnels and areaways | Pipe up to 3": Domestic (US Made) seamless copper tubing (No ERW, longitudinal seam and imported piping are allowed.) | ASTM B88, Seamless | Type L, Hard drawn | Braze with 15% silver content silfloss brazing alloy. Provide threaded connections at unions and valves | ANSI / ASME B16.22, Solder wrought copper |  | Calcium silicate, ASTM C335, K = 0.24 at 75F; Min Service Temp: -20F; Max Service Temp: 450F; Max Moisture Absorption: 0.2% by volume; | See insulation thickness table in the appendix section | 12 ounce / square yard heavy canvas and arabol jacketing + 2 coats of high gloss water-proof white paint | Yellow / Black with arrows in the direction of flow | 1) Insulate valves & associated trim components with fiberglass clamshell, blanket or boxed insulation. 2) Provide preformed clamshell for fittings & valves. Or Approved Equal. 3) Make all provisions necessary to accommodate expansion and contraction caused by temperature variations. (e.g. insulation pillows, thrust blocks, anchors, expansion loops, etc. 3) Submit calculation and results according to the model analyzed with respect to the maximum allowable stresses defined per ASME B31.1 – Power Piping for various materials. | Braze copper pipe joints and non-threaded fittings with 15% silfloss. Threaded fittings shall be soft-soldered using 95/5 lead -free solder. Care should be taken not to anneal the threads. Purge with Nitrogen gas during the brazing process to prevent formation of oxides. Provide provisions for expansion and contraction as necessary to compensate for long pipe runs and high temperatures fluctuations |  | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H26 | HHWS & HHWR | Heating Hot Water Supply & Return mains | Inside utility Tunnels and areaways | Pipe 4" & above: Domestic (US made) Seamless Steel Pipe (No ERW, longitudinal seam and imported piping are allowed.) | ASTM A53-S, Grade A or Grade B Or ASTM A106 Grade B Seamless | Pipe 4" to 10": Schedule 40, Pipe 12" & above: Standard weight | Butt welded AWS D1.1 or flanged. For flanged fittings, use raised face flanges and metal wound gaskets. Mechanical joint couplings required at final connections to equipment to facilitate de-coupling and maintenance. | Standard weight carbon steel, butt weld ASTM B16.9. | pipes up to 2": NIBCO T-585-70-66, pipes 2.5": Apollo series 77-140, pipes 3"- 5": NIBCO LD3122-3. Pipes 6" and above: NIBCO LD3122-5 lug style butterfly valves. Raised full faced spiral wound gaskets and B16 studs and nuts. Isolation valves installed higher than 10' above finished floor shall have chain operated hand wheel. | Calcium silicate, ASTM C335, K = 0.24 at 75F; Min Service Temp: -20F; Max Service Temp: 450F; Max Moisture Absorption: 0.2% by volume; | HVAC | 12 ounce / square yard heavy canvas and arabol jacketing + 2 coats of high gloss water-proof white paint | Yellow / Black with arrows in the direction of flow | provide stem extensions on all ball valves serving insulated pipes to accommodate operation of the valve handle. design engineer or contractor shall analyze the pipe work and make any necessary provisions for thermal expansion and contraction. | Provide provisions for expansion and contraction as necessary to compensate for long pipe runs and high temperatures fluctuations | Steel and copper piping system shall be chemically cleaned and passivated for a minimum of 48 hours. Pressure test piping system with compressed air for a minimum of 24 hours at 150 psig. record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. Neutralize the chemicals and flush the system immediately after cleaning is completed and discharge the chemicals in a code . approved manner in compliance with CIT design guide. Refer to campus design guide document for the details of cleaning & passivation procedures and chemicals. | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H27 | STM | Campus Steam Piping mains | Direct-buried | Domestic (US Made), seamless carbon steel pipe, black welded ends (No ERW, longitudinal seam and imported piping are allowed.) | ASTM A106 Grade B Seamless | Pipe 2.5" to 10": Schedule 40, Pipe 12" & above: Standard weight | Shielded metal arc welding (SMAW) | Fittings:1) Non-flanged Fittings: Class 300# standard weight ANSI / ASTM A234 Malleable iron carbon steel butt welded . 2) Flanged fittings: ASTM A-105 carbon steel 150# class, raised full faced with spiral wound gasket & B16 studs and nuts | up to 2" pipe:800# class, 2.5" and above pipe: 150 # class rising stem gate valves, Make and model # to be approved by Caltech. Isolation valves installed higher than 10' above finished floor shall have chain operated hand wheel. | Calcium Silicate, ASTM C533, ASTM C335, K = 0.38 at 75F; Min Service Temp: 100F; Max Service Temp: 1200F; Max Moisture Absorption: 0.2% by volume; Calsilite Manufacturing Corp only | See insulation thickness table in the appendix section | Pre-engineered system with carrier pipe, casing pipe, insulation and jacketing | Yellow / Black with arrows in the direction of flow | THERE IS A STRONG PREFERENCE TO NOT HAVE ANY DIRECT-BURIED STEAM & STEAM CONDENSATE RETURN PIPES ON CALTECH CAMPUS. SAID PIPES ARE REQUIRED TO BE RUN IN UTILITY TUNNELS INSTEAD. HOWEVER, IT THIS ACCOMMODATION IS NOT PRACTICAL , STEAM & STEAM CONDENSATE RETURN PIPES SHALL BE INSTALLED IN A PRE-ENGINEERED DOUBLE-WALL CONDUIT/CARRIER PIPE SYSTEM. SEE SPECIFIC INFORMATION IN THE PRESSURE TESTING COLUMN.--- 1) Insulate valves & associated trim components with fiberglass clamshell, blanket or boxed insulation. 2) Provide preformed clamshell for fittings & valves. Or Approved Equal. 3) Make all provisions necessary to accommodate expansion and contraction caused by temperature variations. (e.g. insulation pillows, thrust blocks, anchors, expansion loops, etc. 3) Submit calculation and results according to the model analyzed with respect to the maximum allowable stresses defined per ASME B31.1 – Power Piping for various materials. | clean and Chemically Passivate carbon steel pipe. Provide provisions for expansion and contraction as necessary to compensate for long runs and high temperatures fluctuations | 1) Pre-engineered High-Temperature Conduit designed for piping systems below ground and high temperature systems (300 ° F and above). 2) System shall be composed of carbon steel carrier pipe, closed cell mineral wool or or high-temperature foam glass insulation. 3) The insulated pipe is enclosed in an inner conduit casing of 10 gauge steel which is insulated with a high temperature foam glass insulation, rated for 400° F continuous service. 4) The outer layer of foam glass insulation is protected by a heavyweight seamless, high density polyethylene outer jacket. 5) The system is pre-fabricated and pre-engineered as a complete system that is drainable, dryable, and air testable with total manufactured components: pipes, loops, ells, tees, end seals, gland seals, and anchors. 6) The system shall be built to withstand heavy traffic/earth loads, high water tables, and the most corrosive of soils. 7) An ERM leak detection system shall be embedded in the foam glass insulation to detect groundwater intrusion. 8) acceptable manufacturer of pre-engineered pipe work system: Perma-Pipe, Rovanco or Thermacor | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
H28 | SCR | Campus Steam condensate return Piping mains | Direct-buried | Domestic (US Made), seamless carbon steel pipe, black welded ends (No ERW, longitudinal seam and imported piping are allowed.) | ASTM A106 Grade B Seamless | Pipe 2.5" to 10": Schedule 80 | Shielded metal arc welding (SMAW) | Fittings:1) Non-flanged Fittings: Class 300# standard weight ANSI / ASTM A234 Malleable iron carbon steel butt welded . 2) Flanged fittings: ASTM A-105 carbon steel 150# class, raised full faced with spiral wound gasket & B16 studs and nuts | up to 2" pipe:800# class, 2.5" and above pipe: 150 # class rising stem gate valves, Make and model # to be approved by Caltech. Isolation valves installed higher than 10' above finished floor shall have chain operated hand wheel. | Calcium Silicate, ASTM C533, ASTM C335, K = 0.38 at 75F; Min Service Temp: 100F; Max Service Temp: 1200F; Max Moisture Absorption: 0.2% by volume; Calsilite Manufacturing Corp only | See insulation thickness table in the appendix section | 12 ounce / square yard heavy canvas and arabol jacketing + 2 coats of high gloss water-proof white paint | Yellow / Black with arrows in the direction of flow |  |  |  | As per latest applicable CMC, NFPA, FM global and fire marshal requirements. Supports shall be designed for seismic zone 4.
Note on E3: pvaziri:

## Pipe Hanger & Support Spacing
Steel and copper piping system shall be chemically cleaned and passivated for a minimum of 48 hours. Pressure test piping system with compressed air for a minimum of 24 hours at 150 psig. record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. Neutralize the chemicals and flush the system immediately after cleaning is completed and discharge the chemicals in a code . approved manner in compliance with CIT design guide. Refer to campus design guide document for the details of cleaning & passivation procedures and chemicals. ======================================================================Direct buried pipes only: Minimum 3 inch wide polyethylene detectable type marking tape. The tape shall be resistant to alkalis, acids and other destructive agents found in soil and impregnated with metal so that it can be readily recognized after burial by standard locating equipment. 1. Lamination bond of one (1) layer of Minimum 0.35 mils thick aluminum foil between two (2) layers of minimum 4.3 mils thick inert plastic film. 2. Minimum tensile strength: 63 LBS per 3 IN width. 3. Minimum elongation: 500 percent. 4. Provide continuous yellow with black letter printed message repeated every 16 to 36 inches warning of pipe buried below (e.g.: "CAUTION CHILLED WATER BELOW", "CAUTION HEATING HOT WATER BELOW", etc.).
Rovanco's Insul 800 High Temp Conduit is designed for piping systems below ground high temperature systems (210° F and above). It is Drainable, Dryable and Air Testable. The product is composed of a steel, copper, or stainless steel carrier pipe, mineral wool or high temp foam insulation. The insulated pipe is enclosed in an inner conduit casing of 10 gauge steel which is insulated with a high temperature foam insulation, rated for 400° F continuous service. The outer layer of foam insulation is protected by a heavyweight seamless, high density polyethylene outer jacket. This combination results in an economical, high quality, high temp system, and is the most energy efficient system available. Since the system has a polyethylene outer jacket that is non-corrosive, the system does not require Cathodic Protection