## Sheet1
Plumbing fixtures and products table |  | Revision 01
Date: 05/14/2020, Rev-5 |  | Date: 08/19/2020
Plumbing Fixtures and Products Table
item # | Type of fixture | Associated Utilities | Make | Model # | Required mandatory features | Maximum working pressure (PSI) | Max. working temperature (°F) | Country where made | Approvals, codes and/or standards | Means & methods and installation requirements
Plumbing fixtures
PF-01 | Water closet (Floor mounted) | DCW | American Standard | Afwall flowise | ADA complaint, 3641.001 | N/A | N/A | U.S.A. | Non-residential: California Code of Regulations: Title 24 (Building Standards Code); Part 11 (California Green Building Standards Code – aka CAL Green); Chapter 5 (Nonresidential Mandatory Measures), Division 5.3 – Water Efficiency and Conservation; Section 5.303 – Indoor Water Use; 5.303.3 – Water conserving plumbing fixtures and fittings. Residential: California Code of Regulations: Title 24 (Building Standards Code); Part 11 (California Green Building Standards Code – aka CAL Green); Chapter 4 (Residential Mandatory Measures), Division 4.3 – Water Efficiency and Conservation; Section 4.303 – Indoor Water Use; 4.303.1 – Water conserving plumbing fixtures and fittings
PF-02 | Water closet (wall hung) | DCW | American Standard | Afwall flowise | ADA complaint, 2294.001EC | N/A | N/A | U.S.A. |  | with heavy-duty 300 LBS wall carrier
PF-03 | Water closet (tank type) | DCW | American Standard |  | Dual flush tank. ADA complaint | N/A | N/A | U.S.A. |  | For residential installation only, integrated 1.0 GPF
PF-04 | Water closet flush valve | DCW | Sloan | Uppercut standard, WES series | Dual flush , 1.1/1.6 GPF, ADA complaint | N/A | N/A | U.S.A.
PF-05 | Urinal (new construction) | DCW | Zurn | Ecovantage, Z5738.205.00 | 1/8 GPF, ADA complaint, Provide wall cleanout for each urinal | N/A | N/A | U.S.A. |  | with matching battery-powered sensor type flush valve
PF-06 | Urinal (retrofit installation) | DCW | Zurn | Ecovantage, Z5755.205.00 | 1/8 GPF, ADA complaint, Provide wall cleanout for each urinal | N/A | N/A | U.S.A. |  | with matching battery-powered sensor type flush valve
PF-07 | Urinal flush valve | DCW | Zurn | ZTR6203-ULF | Battery powered with custodian service button |  |  | U.S.A.
PF-08 | Lavatory | DCW + DHW | American Standard or Kohler | Kohler LADENA or American Standard OVALYN | Under mount |  |  | U.S.A. |  | Provide angle stop and flexible water supply hose
PF-09 | Lavatory mixing faucet | DCW + DHW | Sloan | Optima EAF-150-ISM | integral spout, Sloan EAF-12, 0.5 GPM flow rate max., temperature mixer for hot and cold, Battery operated, lead free |  |  | U.S.A.
PF-10 | Kitchen sink | DCW + DHW | Elkay | LRAD series | 18 gauge grade 304 Stainless steel, Undermount, ADA compliant, undercoated to dampen sound |  |  | U.S.A. |  | or approved equal by Zurn, Just, etc.
PF-11 | Kitchen faucet | DCW + DHW | Delta or Chicago faucets | DST-101 or 431-MPABCP | 1/2" NPSM water supply inlet connection, lead free |  |  | U.S.A.
PF-12 | Service sink | DCW + DHW | FIAT products | TSBC6010 | with stainless steel MSG wall guards. 12" deep terrazzo service basin |  |  | U.S.A.
PF-13 | Service sink faucet | DCW + DHW | Chicago faucets | 540-LD897SWXFABPC | Lead free |  |  | U.S.A.
PF-14 | Hydration station / drinking fountain | DCW, waste and vent | Elkay | LZS8WSLK | lead-free, single ADA cooler, water filter and bottle filling station |  |  | U.S.A. | UL399, ANSI/NSF 21,53,61 & 372, Green spec listed | provide access panels, in-wall carrier
Plumbing equipment
PE-01 | Industrial hot water heat exchanger | DCW, ICW, IHW, STM and Cond. | CEMLINE, Armstrong, | TBD by design team | Shell & tube heat exchanger, copper tubes, steam trap, temperature controller, steam pressure reducing station, seismic rated support base, etc. | 150 | 300 | U.S.A. | ASME/ANSI
PE-02 | Electric hot water heater | DCW, DHW, DHWR | Bradford-White | size and model # TBD by design team | seismic restraining straps or base, disconnect switch, isolation valves, etc. | 150 |  | U.S.A. |  | To be installed only where natural gas is unavailable
PE-03 | Instantaneous electric hot water heater, mini tank type | DCW, DHW | Stieble Eltron | SHC 2.5 | provide unions and drip catch pan, isolation valves and disconnect switch, 120V, 1300 Watt, 2.5 gallon storage tank, T&P valve | 150 | 210 | U.S.A. |  | To be installed only where building DHW is unavailable
PE-04 | Instantaneous electric hot water heater, point of use , tankless type | DCW, DHW | Stieble Eltron | DHC x-x | provide unions and drip catch pan, isolation valves and disconnect switch. Voltage and wattage to match the requirement of the plumbing fixture being served and local room electric service | 150 | 210 | U.S.A. |  | To be installed only where building DHW is unavailable
PE-05 | Acid waste ejection pump | Chemical waste | Crown-Barnes | size and model # TBD by design team | Submersible, N+1 for redundancy, explosion proof, grinding, alternator/controller, corrosion resistant construction |  |  | U.S.A. |  | As per plans and specifications
PE-06 | Sewage ejection pump | Sanitary waste | Crown-Barnes | size and model # TBD by design team | Submersible, N+1 for redundancy, explosion proof, grinding, alternator/controller, corrosion resistant construction |  |  | U.S.A. |  | As per plans and specifications
PE-07 | Storm drain discharge pump | Storm drain | Crown-Barnes | size and model # TBD by design team | Submersible, duplex, explosion proof, grinding, alternator/controller, corrosion resistant construction | 150 | 200 | U.S.A. |  | As per plans and specifications
PE-08 | Hot water circulation pump | IHWR, DHWR | Grundfos , B&G | size and model # TBD by design team | inline with built-in timer or without timer as per design requirement. Lead-free | 150 | 200 | U.S.A.
PE-09 | Backflow preventer (Plumbing, building main) | DCW, ICW | Deringer | Series 40 | Reduced pressure, all stainless steel construction, lead-free, Deringer Backflows to be installed on 3" and larger systems. Watts backflow preventers are approved only for installation of up to 2". | 175 | 140 | U.S.A. | UL, FM, USC and ASSE | Provide two backflows in parallel for main domestic water service for redundancy. Provide isolation valves with unions or flanges for de-coupling as necessary.
PE-10 |  | DCW, ICW | Watts | Watts 909 |  | 175 | 140 | U.S.A.
PE-11 | [5 empty] | 175 | 140 | U.S.A.
PE-12 | Backflow preventer (fire protection) | Fire water | Ames | C200 or C300 | Double check valve, all Stainless steel construction | 175 | 140 | U.S.A. | UL, FM, USC and ASSE | provide with supervisory switch & butterfly valve. Detector assemblies to be provided only when required by the city of Pasadena
PE-13 |  |  | Zurn/Wilkins | #450 | Double check valve, all Stainless steel construction, allowed only where the N pattern installation is required for compact fit | 175 | 140 | U.S.A.
PE-14 |  |  | Deringer | Series 20 & 30 | Double check valve, all Stainless steel construction |  |  | U.S.A.
PE-15 | Water meter (cold) | DCW, ICW , RCW | Elster | T4000 | With Pulse output option to allow for remote electronic reading and lead-free | 150 | 120 | U.S.A. | AWWS C701 & C708
PE-16 | Water meter (hot) | DHW, IHW | NMT | MultiMag series | With Pulse output option to allow for remote electronic reading and lead-free | 150 | 120 | U.S.A. | AWWS C701 & C708
PE-17 | Natural gas meter | Natural Gas | Sensus | TBD by design team | Provide IMAC domestic meter pulser option. (2 pulse/revolution) |  |  | U.S.A.
PE-18 | Nitrogen meter | Nitrogen | ALICAT | M Series | See Detail section in the DG appendix |  |  | U.S.A.
PE-19 | Pressure regulator (water) | DCW, ICW | Zurn/Wilkins | 500-XL-9SBR | Lead-free, For more details see DG |  |  | U.S.A. | NSF/ANSI/CAN61, IAPMO, CSA, City of Los Angeles and ASSE 1003 | Adjustable from 5-150 PSIG, ≤3" and smaller
PE-20 | Pressure regulator (water) | DCW, ICW | Zurn/Wilkins | ZW109 | Lead-free, For more details see DG |  |  | U.S.A. |  | Adjustable from 5-150 PSIG, ≥4" and larger
PE-21 | Pressure regulator (Compressed air and inert gases) | HPA, LA | McMaster-Carr | 4959K23 or 4959K24 | 5-150 PSI range | 300 | 175 | U.S.A. | N/A | Provide mounting bracket 4910K98
PE-22 | De-ionized water Pressure regulator, Poly-pro material | DI | George Fischer | Type 582 | 7-130 PSI adjustable range, wetted parts polypropylene construction with EPDM diaphrgam and seals | 150 | 120 | U.S.A. | FDA CFR 21 177.2600 | Provide flanged end connections welded at the factory, available from 3/8" -2" sizes
PE-23 | De-ionized water Pressure regulator, Poly-pro material | DI | FilterChem | FC-PPR-50, FC-PPR-75,FC-PPR-10,FC-PPR-15 or FC-PPR-20 as needed | 10-80 PSI adjustable range, polypropylene construction | 100 | 120 | U.S.A. |  | ½" – 1" straight thru flow, 1½" – 2" step down port flow. Provide threaded unions and gauges on both sides of the pressure regulator
Laboratory Plumbing fixtures
LF-01 | Deck mounted mixing faucet | ICW/IHW | Water Saver or Chicago Faucet | to be determined by lab planner or design team based on OPR |  |  |  | U.S.A.
LF-02 | Panel mounted mixing faucet | ICW/IHW | Water Saver or Chicago Faucet |  |  |  |  | U.S.A.
LF-03 | Deck mounted faucet | DI |  |  | Tin-lined only , poly-tubing end connection is not acceptable |  |  | U.S.A. |  | final connection to the fixture shall be stainless tubing and not poly tubing. No mechanical joints allowed inside concealed wall cavities.
LF-04 | Panel mounted faucet | DI |  |  | Tin-lined only , poly-tubing end connection is not acceptable |  |  | U.S.A.
LF-05 | Laboratory natural gas valve | Natural gas | [5 empty] | U.S.A. |  | Natural Gas valves must have AGA certification
LF-06 | Laboratory general purpose gas valve (ball) | Lab Gases | [5 empty] | U.S.A.
LF-07 | Lab general purpose gas valve (needle) | Lab Gases | [5 empty] | U.S.A.
LF-08 | Lab general purpose gas valve (fine control needle) | Lab Gases | [5 empty] | U.S.A.
LF-09 | Emergency eye wash and drench shower | DCW | Haws, Guardian |  |  |  |  | U.S.A.
LF-10 | pressure regulator | Lab Gases | TBD by design group |  |  |  |  | U.S.A.
Plumbing components and parts
PC-01 | local branch Isolation valve 2.5" and smaller (ball) | ICW,IHW,DCW,DHW & inert lab gases | NIBCO or Apollo | NIBCO T-685-66-LF, Apollo 77CLF-140 series | lead free, full ported, MPTxMPT ends, stainless steel trim, 2-piece bronze body | 600 | 400 | U.S.A. | MSS SP-110 | Threaded only, full port, 2-piece, stainless steel trim, blow-out proof
PC-02 | Main isolation valve 3" and larger (butterfly) | ICW,IHW,DCW,DHW | NIBCO or Apollo | LD-3122-3 or LD-3122-5 | lug style ductile iron body, Shall not be installed on steam applications | 250 |  | U.S.A. | MSS-SP67, MSS-SP25 & API-609 | valves 6" and larger must be have gear operated mechanism or LD3122-5, valves 5" and smaller must have lever lock mechanism or LD-3122-3
PC-03 | Angle stop | ICW,IHW,DCW,DHW | Brass Craft | KTR17XC | 1/2" FIP X 3/8" OD compression, Chrome plated | 125 | 180 | U.S.A. | As per manufacturer's listing
PC-04 | Trap primer | DCW, ICW | PPP, Sioux Chief, MIFAB J.R. Smith | TBD by design team | Electronic , adjustable duration and frequency, built-in water hammer arrestor, 120 V AC power | 100 | 140 | U.S.A. | ASSE 1044 | 1/2" MIP X 1/2" MIP
PC-05 | Water hammer arrestor | ICW,IHW,DCW,DHW | PPP, Sioux Chief, MIFAB | TBD by design team | piston operated | 350 | 250 | U.S.A. | ASSE 1010 | 1/2" MPT - 2" MPT
PC-06 | Drinking water inline filter | DCW | Body glove or everpure |  |  |  |  | U.S.A.
PC-07 | Floor sink (general purpose) | Sanitary Waste | ZURN, J.R. Smith | TBD by design team | acid resistant epoxy coated cast iron, sediment bucket, trap prier connection, nickel bronze strainer and Stainless steel screws |  |  | U.S.A.
PC-08 | Floor sink (laboratory) | Sanitary Waste | ZURN, J.R. Smith | TBD by design team | acid resistant epoxy coated cast iron, sediment bucket or dome bottom strainer, trap prier connection, nickel bronze strainer, extra deep receptor and Stainless steel screws |  |  | U.S.A.
PC-09 | Floor sink (mechanical equipment room) | Sanitary Waste | ZURN, J.R. Smith | TBD by design team | Stainless steel construction |  |  | U.S.A.
PC-10 | Floor drain | Sanitary Waste | ZURN, J.R. Smith | TBD by design team | Cast iron , acid resistant interior coating, nickel bronze top & rim & sediment bucket |  |  | U.S.A. |  | All Duco cast iron receptor when appropriate
PC-11 | Garbage disposal unit | Sanitary Waste | MOEN | Host series | 3/4 HP motor, Stainless steel finish, continuous feed & 3 stages of grinding |  |  | U.S.A.
PC-12 | Hose bib | ICW, DCW | MIFAB or approved equal | MHY-90 | Anti-siphon vacuum breaker, cast iron wheel handle & chrome plated brass finish |  |  | U.S.A. | ASSE 1010 | with 1/2" or 3/4" tapered N.P.T. end connection
PC-13 | Balancing valve | DHW, DHWR | Bell & Gossette | Circuit setter | Threaded ends or flanged ends |  |  | U.S.A.
PC-14 | Flange gasket (water) | DCW, DHW | Garlock | 5500 | inorganic fiber with Nitrile binder | 1200 | 550 | U.S.A. | ASTM-F36,F38,F152,F1315, F433 and ASTM-D149
PC-15 | Flange gasket (steam) | Steam, CR | Garlock | FLEXSEAL RWI | spiral wound metallic gasket for raised faced flanges | 1200 | 550 | U.S.A. | ASTM-B16.20 | winding and filler material TBD by design team
PC-16 | ICW and DCW water Pressure regulator | ICW, DCW | Watts | TBD by design team | FNPT X FNPT, lead-free cast copper silicon alloy & integral stainless steel strainer, adjustable from 25PSI - 75 PSI | 180 | 400 | U.S.A. | ASSE 1003, ANSI A112.26.2
PC-17 | Not used | Not used | Not used | Not used | Not used | Not used | Not used | Not used | Not used | Not used
PC-18 | Compressed air pressure regulator | CA | Parker, Wilkerson, Ingersoll Rand or Speed Aire | TBD by design team | Single stage, General purpose, Adjustable from 5-125 PSI ± 1.0 PSI | 300 | 150 | U.S.A. |  | When required, provide parallel filters downstream with isolation valves and unions.
PC-19 | Pressure relief valve | DCW, DHW | Watts or Wilkins | TBD by design team | Adjustable, Brass body |  |  | U.S.A. |  | Set pressure per system requirements
PC-20 | Water supply flexible hose (Faucet) | DCW, DHW, ICW, IHW | Easyflex with safeflow valve | Models number vary based on fixture type being served | Braided 3014 stainless steel jacketing and PVC tubing with integral flood Safe shutoff device | 180 | 125 | U.S.A. | NSF & IAPMO
PC-21 | Water supply flexible hose (water closet) | DCW, RW | Watts | FS-CTC-S-XX | Braided stainless steel jacketing and PVC tubing with integral safeflow anti flood shutoff device | 180 | 125 | U.S.A. | NSF & IAPMO
PC-22 | Floor drain Trap seal | W | MIFAB or approved equal | MI-GARD |  | N/A | 120 | U.S.A. | ASSE 1072 Standard and listed with IAPMO and I.C.C. | From 1.5" to 6" pipe size, 2" height
PC-23 | Natural gas earthquake valve | NG | Little Firefighter | AGV |  | 5 | N/A | U.S.A. | DSA, IAPMO, City of LA | Earthquake valve shall be the same size as the supply pipe entering the building . Provide optional manual reset screws on both sides