## Sheet1
Control Valve selection table
Date: 2023
Rev. 02
Item # | Application media | Symbol | Typical Application | Control valve type | Characterization | Valve action | Construction | Valve body Ends (*#2) | Body style | Actuator type | Actuator position and features (*#3) | Control signal | Make | Rangeability | Minimum close-off pressure | rated min. working pressure (PSI) | comments
1 | Steam | STM | HHW, DHW, IHW and Steam to steam Heat Exchangers, primary side | Globe valve | Linear | Modulating | Cast iron body with stainless trim | Threaded or flanged | 2-way | DDC | Fail to close with spring return | 2-10 V, 0-10 V or 4-20 mA | Belimo, Siemens or J.C. | 1:100 or greater | 30-55 | 150 | control valves shall be sized based on system differential pressure, required system pressure drop, flow rate and valve characterization. Valve manufacturer's recommendations shall also be followed to ensure proper sizing methodology.
2 | Clean steam | CSTM | clean steam humidification, dispersion tube | Globe valve | Modified Equal percentage or =% | Modulating | Stainless steel body and trim | Threaded or flanged | 2-way | DDC | Fail to close with spring return | 2-10 V, 0-10 V or 4-20 mA | Belimo, Siemens, J.C. or Honeywell | 1:100 or greater | 30-55 | 150
3 | Chilled water (FCU +AHU) | CHW | Fan coils and air handling units | Globe valve | Modified Equal percentage or =% | Modulating | Bronze body with Stainless steel trim | Threaded or flanged | 2-way | DDC | Fail to open with spring return | 2-10 V, 0-10 V or 4-20 mA | Belimo, Siemens or J.C. | 1:100 or greater | 30-55 | 150
4 | Heating hot water (FCU+AHU) | HHW | Fan coils and air handling units | Globe valve | Modified Equal percentage or =% | Modulating | Bronze body with Stainless steel trim | Threaded or flanged | 2-way or 3-way | DDC | Fail to close with spring return | 2-10 V, 0-10 V or 4-20 mA | Belimo, Siemens or J.C. | 1:100 or greater | 30-55 | 150
5 | Chilled water and heating hot water (H/X) | CHW & HHW | heat exchanger for chilled beams and radiant panels, primary side | Globe valve | Modified Equal percentage or =% | Modulating | Bronze body with Stainless steel trim | Threaded | 2-way | DDC | Fail to close with spring return. | 2-10 V, 0-10 V or 4-20 mA | Belimo, Siemens or J.C. | 1:100 or greater | 30-55 | 150
6 | Medium temperature chilled water and heating hot water | MCHW & MHHW | chilled beams and radiant panels | characterized ball valve | Modified Equal percentage or =% | 2-position | Bronze body with Stainless steel trim | Threaded | 2-way | DDC | Fail -in-position. See note *#3 regarding HHW | 2-10 V, 0-10 V or 4-20 mA | Belimo, Siemens or J.C. | 1:100 or greater | 30-55 | 150
7 | Heating hot water and chilled water (TAU, etc.) | CHW & HHW | terminal unit reheat coils and stand-alone heating and cooling coils | characterized ball valve | Modified Equal percentage or =% | Modulating | Bronze body with Stainless steel trim | Threaded | 2-way or 3-way | `` | Fail -in-position. See note *#3 regarding HHW | 3-point floating (*#1) | Belimo, Siemens or J.C. | 1:100 or greater | 85 | 150
8 | Process Heating or cooling for high-precision control (e.g. less ± 0.2 DF) | HHW & CHW | For precision control of environments requiring extremely tight temperature control | Globe valve | Modified Equal percentage or =% | Modulating | Stainless steel body and trim | Threaded | 2-way | DDC | Fail to open or closed with spring return as needed | 2-10 V, 0-10 V or 4-20 mA | Siemens | 1:1000 or greater | 30-55 | 150
9 | Process cooling water (H/X) | PCW | PCW heat exchanger, primary side | Globe valve | Modified Equal percentage or =% | Modulating | Bronze body with Stainless steel trim | Threaded | 2-way or 3-way | DDC | Fail to open with spring return | 2-10 V, 0-10 V or 4-20 mA | Belimo, Siemens or J.C. | 1:100 or greater | 30-55 | 150
*#1) 3-point floating control shall only be acceptable for control of HVAC systems in office, administrative and non-laboratory applications.
*#2) Soldered valves are not acceptable
*#3) Heating hot water control valves shall be fail to close with spring return.