## Utilities table
DG Version 5.5 Date: 9/11/2026
Campus Centrally Delivered Utilities Specification Table
Item # | Campus Utility | Point of generation | Static Pressure | Temperature (°F) | Responsibility | Quality | Comments
CU-01 | Campus Steam | From central plant | 50 PSI HPS at @ the building. Pressure reduced inside the building | 377 | Maintained centrally by Central Plant | Saturated steam | Continuously available throughout the year. Building heating hot water is generated from steam-to-hot-water heat exchangers with local building-specific 100% redundant pumping systems (variable speed pumping). Not to be directly used for humidification or sterilization. 70DF superheat applied at Central Plant.
CU-02 | Steam condensate return | central plant | 5-7 PSIG back pressure | 220 | Maintained centrally by Central Plant | N/A | Return to steam condensate main in the tunnel via electric duplex cast iron condensate receiver pump
CU-03 | Chilled water supply | From central and satellite plant | Varies, 90-150 PSIG | 46 | Maintained centrally by Central Plant | N/A | primary pumping only, continuously available throughout the year. Variable volume central plant system - Primary-secondary pumping arrangement is not allowed for chilled water distribution. Contact Central Plant for latest updates. Maintain a 16 degree F temperature differential between Supply and Return Chilled water on the load side.
CU-04 | Chilled water return | From central and satellite plant | Varies, 55-115 PSIG | varies, 52-56 typical | Maintained centrally by Central Plant | N/A
CU-05 | Heating hot water Supply | Mostly local to each building + an existing district heating system in the tunnel | Varies. 30-70 PSIG typical | 150- 180 HHWS temperature and (30 °F) ΔT | Maintained locally at the building by Facilities Operations department | N/A | Each building needs to have its own stand-alone heating hot water heat exchanger and local water chemistry maintained by central plant. When needed, provide a shell and tube heat exchanger skid with duplex circulation pumps, VFDs, controller, traps, chemical pot feeder, air separator, Steam control valve, isolation valves, check valves, insulation, water make-up, water pressure regulator, steam pressure reducing valve, pressure relief valves, etc. for a complete turn-key working system.
CU-06 | Heating hot water Return | Mostly local to each building + an existing district heating system in the tunnel | Varies. 20-40 PSIG typical | 120 - 150 | Maintained locally at the building by Facilities Operations department | N/A
CU-07 | Compressed air | From central plant | 90-110 PSIG | 75-94 | Maintained centrally by central energy plant personnel | Dew Point: 38 °F, particulate: Pre-filter @ 10 Microns, Final Filter @ 2.0 Microns | Compressed air is generated using oil-free compressors
CU-08 | Reverse osmosis water | produced locally in the building or in lab | Varies, TBD by vendor and lab planner | Varies, TBD by vendor and lab planner | Varies, TBD by vendor and lab planner | Varies, TBD by vendor and lab planner | Varies, TBD by vendor and lab planner
CU-09 | De-ionized water | From central plant | 90 PSIG at the point of entrance to the building | N/A | Maintained centrally by central energy plant personnel | Resistivity of 10.0 mega-ohm/cm, with 5.0-10.0 on the pH scale and about 1.0 mega-ohm/cm (0.5 micro-mho/cm) @ the point of delivery to the building | Provide DI water pressure reducing valve at the entrance point to the building set for approximately 30 PSIG
CU-10 | Domestic cold water | From city main | 65-75 PSIG Static | 70 | N/A | See attached PWP water quality table | Provide (2) reduced pressure backflow preventers in parallel
CU-11 | Industrial cold water | produced at the building | 65-75 PSIG Static | 70 | RPBFP assembly maintained locally at the building by FM
CU-12 | Domestic hot water | produced at the building with steam to HHW Heat exchanger | 50-65 PSIG Static | 120 | Maintained locally at the building by Facilities Operations department
CU-13 | Industrial hot water | produced at the building with steam to HHW Heat exchanger | 50-65 PSIG Static | 135 | Maintained locally at the building by Facilities Operations department
CU-14 | Nitrogen | Boil-off from central bulk liquid Nitrogen tank | 100 PSIG | 80-94 | Maintained centrally by Nitrogen Vendor (Air Gas) | Minimum purity ≥ 99.999%, Oxygen ≤ 5 ppm, Carbon Monoxide ≤ 10 ppm, Odor = none | New lab buildings require central Nitrogen meters installed in an accessible location. Nitrogen meter size to be determined during the programming phase.
CU-15 | Fire water | From city main with local fire check assembly | 65-72 PSIG Static | N/A | Check valves maintained centrally by Facilities Operations department |  | Provide double check valve assembly.
CU-16 | Natural Gas | From gas company main line | 8.0" of water column or 1/3 PSIG | N/A | gas meters owned and maintained by Caltech | 1000-1040 BTU/cubic foot @ 60 °F | Provide earthquake valve at the point of entry into the building.
CU-17 | Vacuum | Local in the building or in the lab | 24"-26" HG | N/A | Varies. Division, user group or Facilities Operations department depending on pre-arranged agreements |  | Exact capacity, pressure, make and model # for the vacuum pump shall be determined during lab planning / design phase.
Information provided is current as of date noted. Contact Caltech Project Manager for the latest updates

## PWP water quality
City of Pasadena 2015 Groundwater and MWD Treated Surface Water Data
Parameter | MCL | PHG / MCLG / AL | DLR / MRL | Pasadena Wells Average Range |  | MWD Weymouth Plant Average Range |  |  | MCL Violation | Typical Source of Contaminant
Primary Standard (Monitored for health concerns)
Radiologicals (pCi/L)
Gross Alpha Particle Activi | ty(1) 15 | n/a | 3 | 6.7 <DLR – 17 |  |  | <DLR | <DLR – 4 | No | Erosion of natural deposits
Gross Beta Particle Activit | y(2) 50 | n/a | 4 | 4.4 3.2 – 6.1 |  |  | 5 | 4 – 6 | No | Decay of natural and man-made deposits
Uranium(1) | 20 | 0.43 | 1 | 7.3 4.2 – 15 |  |  | 3 | 3 | No | Erosion of natural deposits
Volatile Organic Compounds
Carbon Tetrachloride (ppt | )(3) 500 | 100 | 500 | 970.0 <DLR – 1340 |  |  | <DLR | <DLR | No | Discharge from chemical plants and other industrial activities
cis-1,2-Dichloroethylene (c-1,2-DCE) (ppb) | 6 | 100 | 0.5 | 0.7 <DLR – 1.12 |  |  | <DLR | <DLR | No | Major biodegradation by-product of TCE and PCE groundwater contamination
Tetrachloroethylene (PCE) | (ppb) 5 | 0.06 | 0.5 | 0.8 <DLR – 2.4 |  |  | <DLR | <DLR | No | Discharge from factories, dry cleaners, and autoshops
Trichloroethylene (TCE) (p | pb) 5 | 1.7 | 0.5 | 1.7 <DLR – 6.5 |  |  | <DLR | <DLR | No | Discharge from metal degreasing sites and other factories
Inorganic Compounds
Aluminum (ppb)(4) | 1000 | 600 | 50 | <DLR | <DLR – 41 |  | 156 | 88 – 200 | No | Erosion of natural deposits
Barium (ppb)(4) | 1000 | 2000 | 100 | 68.6 | 22 – 170 |  | 122 | 122 | No | Erosion of natural deposits
Chromium (ppb)(4) | 50 | -100 | 0.2 | 3.6 | <DLR – 6.3 |  | <DLR | <DLR | No | Erosion of natural deposits
Chromium VI (ppb) | 10 | 0.02 | 1 | 3.4 | 1.1 – 7.2 |  | <DLR | <DLR | No | Erosion of natural deposits, industrial waste discharge
Fluoride (ppm) | 2 | 1 | 0.1 | 0.9 | 0.3 – 1.5 |  | 0.7 | 0.6 – 1.0 | No | Water additive for dental health, erosion of natural deposit
Nitrate (ppm)(3) | 45 | 45 | 0.4 | 28.4 | 12.9 – 55.6 |  | <DLR | <DLR | No | Runoff and leaching from fertilizer use, erosion of natural deposits
Perchlorate (ppb)(3) | 6 | 1 | 4 | 9.8 | <DLR – 17.4 |  | <DLR | <DLR | No | Industrial waste discharge
Secondary Standard (Monitored for aesthetic qualities such as taste, color, odor)(5)
Chloride (ppm) | 500 | n/a | n/a | 46.7 | 16.4 – 96.6 |  | 100 | 98 – 102 | No | Runoff and leaching from natural deposits
Color (Units) | 15 | n/a | n/a | 3.1 | 1 – 5 |  | 1 | 1 | No | Naturally-occurring organic materials
Odor (Units) | 3 | n/a | 1 | 0.0 0 |  |  | 2 | 2 | No | Naturally-occurring organic materials
Specific Conductance (µS/ | cm) 1600 | n/a | n/a | 748.0 504 – 1087 |  |  | 1040 | 1030 – 1060 | No | Substances that form ions when in water
Sulfate (ppm) | 500 | n/a | 0.5 | 84.0 27.3 – 149 |  |  | 257 | 252 – 261 | No | Runoff and leaching from natural deposits
Total Dissolved Solids (pp | m) 1000 | n/a | n/a | 477.2 298 – 698 |  |  | 660 | 654 – 665 | No | Runoff and leaching from natural deposits
Turbidity (NTU) | 5 | n/a | 0.1 | 0.3 0.14 – 0.61 |  |  | <DLR | <DLR | No | Soil runoff
Other Parameters
123-Trichloropropane (pp | t) n/a | 0.7 | 5 | <DLR | <DLR – 7.5 |  | NA | NA | No | Industrial waste discharge
Alkalinity (ppm) | n/a | n/a | n/a | 177.8 | 110 – 206 |  | 126 | 123 – 129 | No | n/a
Calcium (ppm) | n/a | n/a | n/a | 79.1 | 43.3 – 123 |  | 78 | 77 – 78 | No | n/a
Corrosivity (LSI) | n/a | n/a | n/a | 0.08 | -0.09 – 0.25 |  | 0.57 | 0.56 – 0.58 | No | n/a
Magnesium (ppm) | n/a | n/a | n/a | 23.7 | 10.7 – 37.8 |  | 27 | 26 – 28 | No | n/a
pH (pH Units) | n/a | n/a | n/a | 7.5 | 7.1 – 7.95 |  | 8.1 | 8.1 | No | n/a
Potassium (ppm)(6) | n/a | n/a | n/a | 2.7 | 2.5 – 2.9 |  | 4.9 | 4.8 – 5.0 | No | n/a
Sodium (ppm) | n/a | n/a | n/a | 31.3 | 23 – 36 |  | 100 | 97 – 102 | No | n/a
Understanding the Water Quality Chart
Maximum Contaminant Level (MCL): The highest level of a contaminant that is allowed in drinking water. Primary MCLs are set as close to the PHGs (or MCLGs) as is economically and technologically feasible. Secondary MCLs are set to protect the odor, taste, and appearance of drinking water.
Maximum Contaminant Level Goal (MCLG): The level of a
contaminant in drinking water below which there is no known or expected risk to health. MCLGs are set by the USEPA.
Public Health Goal (PHG): The level of a contaminant in drinking water below which there is no known or expected risk to health. PHGs are set by the California Environmental Protection Agency. Maximum Residual Disinfectant Level (MRDL): The highest level of a disinfectant allowed in drinking water. There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants.
Primary Drinking Water Standard (PDWS): MCLs and MRDLs for contaminants that affect health along with their monitoring and reporting requirements, and water treatment requirements. Maximum Residual Disinfectant Level Goal (MRDLG): The level of a drinking water disinfectant below which there is no known or expected risk to health. MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants.
Detection Limits for Purposes of Reporting (DLR): The DLR is a parameter that is set by regulation for each reportable analyte. It is not laboratory specific and it is independent of the analytical method used (in cases where several methods are approved). It is expected that a laboratory can achieve a Reporting Limit that is lower than or equal to the DLR set by the DDW. This is also known as the Minimum Reporting Level (MRL).
NA: Contaminant or property was not analyzed.
n/a: Not applicable.
ND: Contaminant was not detected. The contaminant is less than the DLR.
Regulatory Action Level (AL): The concentration of a contaminant which, if exceeded, triggers treatment or other requirements that a water system must follow.
Units of Measurement:
ppm = parts per million ppb = parts per billion ppt = parts per trillion pCi/L = picocuries per liter LSI = Langelier Saturation Index
µS/cm = microsiemens per centimeter
NTU = Nephelometric Turbidity Units.