## Sheet1
DG Version 5.5 Date: 9/11/2026
Plumbing Fixtures and Products Table
item # | Type of fixture | Associated Utilities | Make | Model # | Required mandatory features | Maximum working pressure (PSI) | Max. working temperature (°F) | Country where made | Approvals, codes and/or standards | Means & methods and installation requirements
Plumbing fixtures
PF-01 | Water closet (Floor mounted) | DCW | American Standard | Afwall flowise | ADA complaint, 3641.001 | N/A | N/A | U.S.A. | Non-residential: California Code of Regulations: Title 24 (Building Standards Code); Part 11 (California Green Building Standards Code – aka CAL Green); Chapter 5 (Nonresidential Mandatory Measures), Division 5.3 – Water Efficiency and Conservation; Section 5.303 – Indoor Water Use; 5.303.3 – Water conserving plumbing fixtures and fittings. Residential: California Code of Regulations: Title 24 (Building Standards Code); Part 11 (California Green Building Standards Code – aka CAL Green); Chapter 4 (Residential Mandatory Measures), Division 4.3 – Water Efficiency and Conservation; Section 4.303 – Indoor Water Use; 4.303.1 – Water conserving plumbing fixtures and fittings | For use only where allowed. Obtain CIT facilities engineer approval.
PF-02 | Water closet (wall hung) | DCW | American Standard | Afwall flowise | ADA complaint, 2294.001EC | N/A | N/A | U.S.A. |  | with heavy-duty 300 LBS wall carrier. For new construction applications.
PF-03 | Water closet (tank type) | DCW | American Standard |  | Dual flush tank. ADA complaint | N/A | N/A | U.S.A. |  | For residential installation only, integrated 1.0 GPF
PF-04 | Water closet flush valve | DCW | Sloan | Uppercut standard, WES series | Dual flush , 1.1/1.6 GPF, ADA complaint | N/A | N/A | U.S.A.
PF-05 | Urinal (new construction) | DCW | Zurn | Ecovantage, Z5738.205.00 | 1/8 GPF, ADA complaint, Provide wall cleanout for each urinal and install per current CPC | N/A | N/A | U.S.A. |  | with matching battery-powered sensor type flush valve
PF-06 | Urinal (retrofit installation) | DCW | Zurn | Ecovantage, Z5755.205.00 | 1/8 GPF, ADA complaint, Provide wall cleanout for each urinal and install per current CPC | N/A | N/A | U.S.A. |  | with matching battery-powered sensor type flush valve
PF-07 | Urinal flush valve | DCW | Zurn | ZTR6203-ULF | Battery powered with custodian service button |  |  | U.S.A.
PF-08 | Lavatory | DCW + DHW | American Standard or Kohler | Kohler LADENA or American Standard OVALYN | Under mount |  |  | U.S.A. |  | Provide angle stop and flexible water supply hose
PF-09 | Lavatory mixing faucet | DCW + DHW | Sloan | Optima EAF-100-ISM | integral spout, Sloan EAF-12, 0.5 GPM flow rate max, temperature mixer for hot and cold, hardwired operated, lead free. Installed in major renovation projects where convenience outlets are readily available or will be installed as part of the project. |  |  | U.S.A. |  | For new construction and renovation projects.
PF-10 | Kitchen sink | DCW + DHW | Elkay | ELUHAD | 18 gauge grade 304 Stainless steel, Undermount, ADA compliant, undercoated to dampen sound. Minimum depth: 5.375". |  |  | U.S.A. |  | or approved equal by Zurn, Just, etc.
PF-11 | Kitchen faucet | DCW + DHW | Delta or Chicago faucets | DST-101 or 431-MPABCP | 1/2" NPSM water supply inlet connection, lead free & 0.5 GPM aerator |  |  | U.S.A.
PF-12 | Service sink | DCW + DHW | FIAT products | TSBC6010 | with stainless steel MSG wall guards. 12" deep terrazzo service basin |  |  | U.S.A.
PF-13 | Service sink faucet | DCW + DHW | Chicago faucets | 540-LD897SWXFABCP | Lead free |  |  | U.S.A.
PF-14a | Hydration station / drinking fountain | DCW, waste and vent | Elkay or Oasis | LZSTLDDWSSK or PGSBFSL | lead-free, two station, ADA cooler, water filter, non-refrigerated, bottle filling station |  |  | U.S.A. | UL399, ANSI/NSF 42,53,61 & 372, Green spec listed | provide access panels, provide in-wall carrier
PF-14b | Hydration station / drinking fountain | DCW, waste and vent | Elkay or Oasis | LZSTL8WSSK PG8SBFSL | lead-free, two station, ADA cooler, water filter, refrigerated, bottle filling station |  |  | U.S.A. | UL399, ANSI/NSF 42,53,61 & 372, Green spec listed | provide access panels, provide in-wall carrier.
PF-15 | Mop sink faucet | DCW + DHW | Chicago faucets | 897-CPP | integral check valves and vacuum breaker, chrome plated finish |  |  | U.S.A. | ASME A112.18.1/CSA B125.1
PF-16 | Shower stall control valve | DCW + DHW | Moen | Posi-Temp 2590 | 1/2" IPS connections, pressure balancing valve with integral stops |  |  | U.S.A. | ASME A112.18.1/CSA B125.1, ASSE 1016 | Install at each point of use. The maximum water temperature discharging from an individual showerhead shall be limited to 120°F.
Plumbing equipment
PE-01 | Industrial hot water heat exchanger | DCW, ICW, IHW, STM and Cond. | CEMLINE, Armstrong, | TBD by design team | Shell & tube heat exchanger, copper tubes, steam trap, temperature controller, steam pressure reducing station, seismic rated support base, etc. | 150 | 300 | U.S.A. | ASME/ANSI
PE-02 | Electric hot water heater | DCW, DHW, DHWR | Bradford-White | size and model # TBD by design team | seismic restraining straps or base, disconnect switch, isolation valves, etc. | 150 |  | U.S.A. |  | To be installed only where natural gas is unavailable
PE-03 | Instantaneous electric hot water heater, mini tank type | DCW, DHW | Stieble Eltron | SHC 2.5 | provide unions and drip catch pan, isolation valves and disconnect switch, 120V, 1300 Watt, 2.5 gallon storage tank, T&P valve | 150 | 210 | U.S.A. |  | To be installed only where building DHW is unavailable
PE-04 | Instantaneous electric hot water heater, point of use , tankless type | DCW, DHW | Stieble Eltron | DHC x-x | provide unions and drip catch pan, isolation valves and disconnect switch. Voltage and wattage to match the requirement of the plumbing fixture being served and local room electric service | 150 | 210 | U.S.A. |  | To be installed only where building DHW is unavailable
PE-05 | Acid waste ejection pump | Chemical waste | Crown-Barnes | size and model # TBD by design team | Submersible, N+1 for redundancy, explosion proof, grinding, alternator/controller, corrosion resistant construction |  |  | U.S.A. |  | As per plans and specifications
PE-06 | Sewage ejection pump | Sanitary waste | Crown-Barnes | size and model # TBD by design team | Submersible, N+1 for redundancy, explosion proof, grinding, alternator/controller, corrosion resistant construction |  |  | U.S.A. |  | As per plans and specifications
PE-07 | Storm drain discharge pump | Storm drain | Crown-Barnes | size and model # TBD by design team | Submersible, duplex, explosion proof, grinding, alternator/controller, corrosion resistant construction | 150 | 200 | U.S.A. |  | As per plans and specifications
PE-08 | Hot water circulation pump | IHWR, DHWR | Grundfos , B&G | size and model # TBD by design team | in line with built-in timer or without timer as per design requirement. Lead-free | 150 | 200 | U.S.A.
PE-09 | Backflow preventer (Plumbing, building main) | DCW, ICW | Deringer | Series 40 | Reduced pressure, all stainless steel construction, lead-free, Deringer Backflows to be installed on 3" and larger systems. Watts backflow preventers are approved only for installation of up to 2". | 175 | 140 | U.S.A. | UL, FM, USC and ASSE | Provide two backflows in parallel for main domestic water service for redundancy. Provide isolation valves with unions or flanges for de-coupling as necessary.
PE-10 |  | DCW, ICW | Watts | Watts 909 |  | 175 | 140 | U.S.A.
PE-11 | [5 empty] | 175 | 140 | U.S.A.
PE-12 | Backflow preventer (fire protection) | Fire water | Ames | C200 or C300 | Double check valve, all Stainless steel construction | 175 | 140 | U.S.A. | UL, FM, USC and ASSE | provide with supervisory switch & butterfly valve. Detector assemblies to be provided only when required by the city of Pasadena
PE-13 |  |  | Zurn/Wilkins | #450 | Double check valve, all Stainless steel construction, allowed only where the N pattern installation is required for compact fit | 175 | 140 | U.S.A.
PE-14 |  |  | Deringer | Series 20 & 30 | Double check valve, all Stainless steel construction |  |  | U.S.A.
PE-15 | Water meter (cold) | DCW, ICW , RCW | Elster | T4000 | With Pulse output option to allow for remote electronic reading and lead-free | 150 | 120 | U.S.A. | AWWS C701 & C708
PE-16 | Water meter (hot) | DHW, IHW | NMT | MultiMag series | With Pulse output option to allow for remote electronic reading and lead-free | 150 | 120 | U.S.A. | AWWS C701 & C708
PE-17 | Natural gas meter | Natural Gas | Sensus | TBD by design team | Provide IMAC domestic meter pulser option. (2 pulse/revolution) |  |  | U.S.A.
PE-18 | Nitrogen meter | Nitrogen | ALICAT | M Series | See Detail section in the DG appendix |  |  | U.S.A.
PE-19 | Pressure regulator (water) | DCW, ICW | Zurn/Wilkins | 500-XL-9SBR | Lead-free, For more details see DG |  |  | U.S.A. | NSF/ANSI/CAN61, IAPMO, CSA, City of Los Angeles and ASSE 1003 | Adjustable from 5-150 PSIG, ≤3" and smaller
PE-20 | Pressure regulator (water) | DCW, ICW | Zurn/Wilkins | ZW109 | Lead-free, For more details see DG |  |  | U.S.A. |  | Adjustable from 5-150 PSIG, ≥4" and larger
PE-21 | Pressure regulator (Compressed air and inert gases) | HPA, LA | McMaster-Carr | 4959K53 or 4959K54 | 5-150 PSI range | 300 | 175 | U.S.A. | N/A | Provide mounting bracket 4910K98
PE-22 | De-ionized water Pressure regulator, Poly-pro material | DI | George Fischer | Type 582 | 7-130 PSI adjustable range, wetted parts polypropylene construction with EPDM diaphragm and seals | 150 | 120 | U.S.A. | FDA CFR 21 177.2600 | Provide flanged end connections welded at the factory, available from 3/8" -2" sizes
Laboratory Plumbing fixtures
LF-01 | Deck mounted mixing faucet | ICW/IHW | Water Saver or Chicago Faucet | to be determined by lab planner or design team based on OPR |  |  |  | U.S.A.
LF-02 | Panel mounted mixing faucet | ICW/IHW | Water Saver or Chicago Faucet |  |  |  |  | U.S.A.
LF-03 | Deck mounted faucet | DI |  |  | Tin-lined only , poly-tubing end connection is not acceptable |  |  | U.S.A. |  | final connection to the fixture shall be stainless tubing and not poly tubing. No mechanical joints allowed inside concealed wall cavities.
LF-04 | Panel mounted faucet | DI |  |  | Tin-lined only , poly-tubing end connection is not acceptable |  |  | U.S.A.
LF-05 | Laboratory natural gas valve | Natural gas | TBD by design group |  |  |  |  | U.S.A. |  | Natural Gas valves must have AGA certification
LF-06 | Laboratory general purpose gas valve (ball) | Lab Gases | [5 empty] | U.S.A.
LF-07 | Lab general purpose gas valve (needle) | Lab Gases | [5 empty] | U.S.A.
LF-08 | Lab general purpose gas valve (fine control needle) | Lab Gases | [5 empty] | U.S.A.
LF-09 | Emergency eye wash and drench shower | DCW | Haws, Guardian |  |  |  |  | U.S.A.
LF-10 | Pressure regulator | Lab Gases | TBD by design group |  |  |  |  | U.S.A.
Plumbing components and parts
PC-01 | local branch Isolation valve 2.5" and smaller (ball) | ICW,IHW,DCW,DHW & inert lab gases | NIBCO or Apollo | NIBCO T-685-66-LF, Apollo 77CLF-140 series | lead free, full ported, MPTxMPT ends, stainless steel trim, 2-piece bronze body | 600 | 400 | U.S.A. | MSS SP-110 | Threaded only, full port, 2-piece, stainless steel trim, blow-out proof
PC-02 | Main isolation valve 3" and larger (butterfly) | ICW,IHW,DCW,DHW | NIBCO or Apollo | LD-3122-3 or LD-3122-5 | lug style ductile iron body, Shall not be installed on steam applications | 250 |  | U.S.A. | MSS-SP67, MSS-SP25 & API-609 | valves 6" and larger must be have gear operated mechanism or LD3122-5, valves 5" and smaller must have lever lock mechanism or LD-3122-3
PC-03 | Angle stop | ICW,IHW,DCW,DHW | Brass Craft | KTR17XC | 1/2" FIP X 3/8" OD compression, Chrome plated | 125 | 180 | U.S.A. | As per manufacturer's listing
PC-04 | Trap primer | DCW, ICW | PPP, Sioux Chief, MIFAB J.R. Smith | TBD by design team | Electronic , adjustable duration and frequency, built-in water hammer arrestor, 120 V AC power | 100 | 140 | U.S.A. | ASSE 1044 | 1/2" MIP X 1/2" MIP
PC-05 | Water hammer arrestor | ICW,IHW,DCW,DHW | PPP, Sioux Chief, MIFAB | TBD by design team | piston operated | 350 | 250 | U.S.A. | ASSE 1010 | 1/2" MPT - 2" MPT
PC-06 | Drinking water inline filter | DCW | Body glove or everpure |  |  |  |  | U.S.A.
PC-07 | Floor sink (general purpose) | Sanitary Waste | ZURN, J.R. Smith | TBD by design team | acid resistant epoxy coated cast iron, sediment bucket, trap prier connection, nickel bronze strainer and Stainless steel screws |  |  | U.S.A.
PC-08 | Floor sink (laboratory) | Sanitary Waste | ZURN, J.R. Smith | TBD by design team | acid resistant epoxy coated cast iron, sediment bucket or dome bottom strainer, trap prier connection, nickel bronze strainer, extra deep receptor and Stainless steel screws |  |  | U.S.A.
PC-09 | Floor sink (mechanical equipment room) | Sanitary Waste | ZURN, J.R. Smith | TBD by design team | Stainless steel construction |  |  | U.S.A.
PC-10 | Floor drain | Sanitary Waste | ZURN, J.R. Smith | TBD by design team | Cast iron , acid resistant interior coating, nickel bronze top & rim & sediment bucket |  |  | U.S.A. |  | All Duco cast iron receptor when appropriate
PC-11 | Garbage disposal unit | Sanitary Waste | MOEN | Host series | 3/4 HP motor, Stainless steel finish, continuous feed & 3 stages of grinding |  |  | U.S.A.
PC-12 | Hose bib | ICW, DCW | MIFAB or approved equal | MHY-90 | Anti-siphon vacuum breaker, cast iron wheel handle & chrome plated brass finish |  |  | U.S.A. | ASSE 1010 | with 1/2" or 3/4" tapered N.P.T. end connection
PC-13 | Balancing valve | DHW, DHWR | Bell & Gossett | Circuit setter | Threaded ends or flanged ends |  |  | U.S.A.
PC-14 | Flange gasket (water) | DCW, DHW | Garlock | 5500 | inorganic fiber with Nitrile binder | 1200 | 550 | U.S.A. | ASTM-F36,F38,F152,F1315, F433 and ASTM-D149
PC-15 | Flange gasket (steam) | Steam, CR | Garlock | FLEXSEAL RWI | spiral wound metallic gasket for raised faced flanges | 1200 | 550 | U.S.A. | ASTM-B16.20 | winding and filler material TBD by design team
PC-16 | ICW and DCW water Pressure regulator | ICW, DCW | Watts | TBD by design team | FNPT X FNPT, lead-free cast copper silicon alloy & integral stainless steel strainer, adjustable from 25PSI - 75 PSI | 180 | 400 | U.S.A. | ASSE 1003, ANSI A112.26.2
PC-17 | Not used | Not used | Not used | Not used | Not used | Not used | Not used | Not used | Not used | Not used
PC-18 | Compressed air pressure regulator | CA | Parker, Wilkerson, Ingersoll Rand or Speed Aire | TBD by design team | Single stage, General purpose, Adjustable from 5-125 PSI ± 1.0 PSI | 300 | 150 | U.S.A. |  | When required, provide parallel filters downstream with isolation valves and unions.
PC-19 | Pressure relief valve | DCW, DHW | Watts or Wilkins | TBD by design team | Adjustable, Brass body |  |  | U.S.A. |  | Set pressure per system requirements
PC-20 | Water supply flexible hose (Faucet) | DCW, DHW, ICW, IHW | Easyflex with safe Flow valve | Models number vary based on fixture type being served | Braided 3014 stainless steel jacketing and PVC tubing with integral flood Safe shutoff device | 180 | 125 | U.S.A. | NSF & IAPMO
PC-21 | Water supply flexible hose (water closet) | DCW, RW | Watts | FS-CTC-S-XX | Braided stainless steel jacketing and PVC tubing with integral safeflow anti flood shutoff device | 180 | 125 | U.S.A. | NSF & IAPMO
PC-22 | Floor drain Trap seal | W | MIFAB or approved equal | MI-GARD |  | N/A | 120 | U.S.A. | ASSE 1072 Standard and listed with IAPMO and I.C.C. | From 1.5" to 6" pipe size, 2" height
PC-23 | Natural gas earthquake valve | NG | Little Firefighter | AGV |  | 5 | N/A | U.S.A. | DSA, IAPMO, City of LA | Earthquake valve shall be the same size as the supply pipe entering the building . Provide optional manual reset screws on both sides
PC-24 | Undercounter mixing valve | DCW, DHW, ICW, IHW | Guardian/Watts | Series LFUSG-B-M2 | Lead free, threaded connections, includes integral check valves, integral screens and an adjustment nut with locking feature. | 150 | 120 | U.S.A. | ASSE 1070 Standard, IAPMO cUPC | Provide additional external check valves