## Plumbing Piping
DG Version 5.5 Date: 9/11/2026
No | Abbreviation | Service | Location | Pipe Material | Class / Compliance /approval | Type | Joint | Fittings | Valves*2 | Insulation Material | Insulation Size | Jacket | Background Color / Letter Color | Remarks | Special Handling | Pressure Testing / Chemically Cleaning or Passivation | Rod Size / Hangers Spacing
P1 | DCW or ICW, Option #1 | Domestic Cold Water Supply or Industrial Cold Water Supply | Direct Buried, Below Grade | Pipes 4" & above: AWWA C900 PVC pipe, DR18 / 200 PSI pressure class | Material cell classification material cell 12454-8 per ASTM D 1784. NSF/ANSI 61 : Drinking Water System components - Health Effects. NSF/ANSI 372 : Drinking Water System Components – Lead-free content | PVC | Provide polyvinyl chloride (PVC) couplings with twin elastomeric gaskets / retaining glands which are designed to connect straight ends of plain pipe and allow 2 degrees of deflection at each gasket for a total of 4 degrees per coupling. | Ductile iron fittings or AWWA-C900 PVC | Pipes up to 2": NIBCO T-585-70-66-LF Pipes 2.5": NIBCO T-585-66-LF Pipes 3"- 5": NIBCO LD3122-3. Pipes 6" and above: NIBCO LD3122-5 lug style butterfly valves. Raised full faced spiral wound gaskets and B16 studs and nuts. All components associated with potable water system shall be lead-free. | N/A | N/A |  | DCW: Green / White ---------------------ICW: Green / white | Install concrete anchor thrust blocks or tie-rods on all underground lines at all tees and elbows to prevent movement when under pressure. All tie-rods, clamps, brackets, and bolts shall be ductile iron, stainless steel, galvanized or epoxy coated. Flanged restraints shall be similar to "MEGALUG series 1100 or 1700 series". | Pipe supported on firm sand bed for entire length. [CPC 314.3] No rocks supporting or touching pipes. [CPC 315.4] Six inches of sand bed minimum for copper, or PVC pipe per manufacturer's recommendation, No rocks or debris in first 12” of backfill over ABS pipe. [CPC 315.4] Trenches not to undermine footings within bearing plane (45˚) [CPC 315.1] Sewer and water pipe to be buried minimum 18” deep. [CPC 609.1] | Ductile iron, PVC and copper piping system shall be chemically cleaned for a minimum of 48 hours. Pressure test piping system either hydrostatically with water as the testing medium or pnuematically with either compressed air or nitrogen as the testing medium. Pipes smaller than and equal to 2.5" diameter shall be tested using either the hydrostatic or pneumatic methods. Pipes larger than 2.5" diameter shall be tested using a combination of hydrostatic and pnuematic testing using 95% water by volume and 5% compressed air to minimize any potential risks posed by stored energy in compressed air. Pipes shall be tested with a pressure of not less than 1.5 times the operating pressure but not less than 100 psig. Test pressure shall be held for a minimum period of 24 hours. Record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. Neutralize the chemicals and flush the system immediately after cleaning is completed and discharge the chemicals in accordance with the local codes and in compliance with CIT design guide. Refer to campus design guide document for the details of cleaning & passivation procedures and chemicals. PVC and other plastic pipes do not need to be passivated. Sterilize the entire potable water system. See Appendix section for details. | N/A
P2 | DCW or ICW, Option #2 | Domestic Cold Water Supply or Industrial Cold Water Supply | Direct Buried, Below Grade | Pipes 4" & above: Cement-lined and seal coated ductile iron, Class 53 or 54 with polyethylene encasement, asphaltic coated on the outside. | Cement lined detailed iron pipe. ANSI/AWWA, C151/A21.51. NSF/ANSI 61: Drinking Water System components - Health Effects. NSF/ANSI 372: Drinking Water System Components – Lead-free content | Ductile iron | Mechanical joints, "MEGALUG series 1100TDM" or "MEGALUG series 1700" as appropriate for the application and joint type | Provide ductile iron fittings conforming to AWWA C110 with a minimum rated working pressure of 350 psi. Provide fittings with bells and gaskets specifically designed for cast iron equivalent outside diameter PVC pipe. Use mechanical joint fittings or fittings with bells and gasket ends. | Pipes up to 2": NIBCO T-585-70-66-LF Pipes 2.5": NIBCO T-585-66-LF Pipes 3"- 5": NIBCO LD3122-3. Pipes 6" and above: NIBCO LD3122-5 lug style butterfly valves. Raised full faced spiral wound gaskets and B16 studs and nuts. All components associated with potable water system shall be lead-free | N/A | N/A |  | DCW: Green / White ---------------------ICW: Green / white |  |  |  | N/A
P3 | DCW or ICW | Domestic Cold Water Supply or Industrial Cold Water Supply | Direct Buried, Below Grade | Pipe 1.5" to 3": Copper tubing | ASTM B88. NSF/ANSI 61 : Drinking Water System components - Health Effects. NSF/ANSI 372 : Drinking Water System Components – Lead-free content | Type K, rigid hard drawn | 1) Braze with 15% silver content "Sil-Fos" brazing alloy. 2) Provide FxF threaded unions and FxF threaded isolation valves. | 1) Wrought copper solder sweat type, ANSI B16.22 or brass castings, ANSI B16.18. 2) Press fittings as manufactured by Viega "ProPress", Mueller "Streamline" PRS, or Elkhart "Apollo Press" | Pipes up to 2": NIBCO T-585-70-66-LF, Pipes 2.5": NIBCO T-585-66-LF Pipes 3"- 5": NIBCO LD3122-3. Pipes 6" and above: NIBCO LD3122-5 lug style butterfly valves. Raised full faced spiral wound gaskets and B16 studs and nuts. All components associated with potable water system shall be lead-free | N/A | N/A | Field wrap with 30 mil PVC tape or 30 mil polyethylene sleeving, blue color | DCW: Green / White ---------------------ICW: Green / white | All internal components exposed to potable water shall be of lead-free construction as per California AB-1953. Sterilize the system by introducing chlorinating solution into the entire system for a minimum period of 24 hours. Maintain concentration of 50-150 ppm. Residual chlorine not to exceed 0.2 ppm. Braze copper pipe joints and non-threaded fittings with 15% "Sil-Fos". Purge with Nitrogen gas during the brazing process to prevent formation of oxides. | Same as above |  | N/A
P4 | DCW or ICW | Domestic Cold Water Supply or Industrial Cold Water Supply | Direct Buried, Below Grade | Pipe 0.5" to 1": Soft-temper copper (Residential installations only) | ASTM B88. NSF/ANSI 61 : Drinking Water System components - Health Effects. NSF/ANSI 372 : Drinking Water System Components – Lead-free content | Type K, hard drawn | 1) Braze with 15% silver content "Sil-Fos" brazing alloy. 2) Provide FxF threaded unions and FxF threaded isolation valves. | 1) Wrought copper solder sweat type, ANSI B16.22 or brass castings, ANSI B16.18. 2) Press fittings as manufactured by Viega "ProPress", Mueller "Streamline" PRS, or Elkhart "Apollo Press" | Pipe up to 1": NIBCO T685-66-LF ball valves | N/A | N/A | Field wrap with 30 mil PVC tape or 30 mil polyethylene sleeving, blue color | DCW: Green / White ---------------------ICW: Green / white | All internal components exposed to potable water shall be of lead-free construction as per California AB-1953 |  |  | N/A
P5 | DCW, ICW or SCW | Domestic Cold Water Supply, Industrial Cold Water Supply or soft cold water | Above Ground | Pipes up to 4": Seamless copper tubing (No ERW, longitudinal seam and imported piping are allowed.) | ASTM B88. NSF/ANSI 61 : Drinking Water System components - Health Effects. NSF/ANSI 372 : Drinking Water System Components – Lead-free content | Type L, hard drawn, hot temper | 1) Braze with 15% silver content "Sil-Fos" brazing alloy. 2) Provide FxF threaded unions and FxF threaded isolation valves. 3) Exposed to view at plumbing fixtures and finished equipment, satin finish CP brass pipe with threaded cast bronze fittings. 4) No soft solder allowed except within 6" of threaded couplings. | 1) Wrought copper solder sweat type, ANSI B16.22 or brass castings, ANSI B16.18 2) Press fittings as manufactured by Viega "ProPress", Mueller "Streamline" PRS, or Elkhart "Apollo Press" | Pipes up to 2": NIBCO T-585-70-66-LF Pipes 2.5": NIBCO T-585-66-LF Pipes 3"- 5": NIBCO LD3122-3. Pipes 6" and above: NIBCO LD3122-5 lug style butterfly valves. Raised full faced spiral wound gaskets and B16 studs and nuts. All components associated with potable water system shall be lead-free. Isolation valves installed higher than 10' above finished floor shall have chain operated hand wheel | N/A | N/A | N/A | DCW: Green / White ---------------------ICW: Green / white | Run mains at evenly pitched 1 inch in 50 feet. Make allowance for expansion in all piping installation so that the usual variation in temperature will not cause stress at any point. Securely anchor where necessary to distribute expansion stresses. Provide 3/4" drainage valve at low points. Anchor all lines and risers as necessary to prevent noise or vibration when water is turned on or off. Separately valve each branch and riser. Make all such valves accessible with approved type panels. Balance, vent, and adjust piping to provide circulation to all fixtures and to prevent water hammer. | Braze copper pipe joints and non-threaded fittings with 15% "Sil-Fos". Threaded fittings shall be soft-soldered using 95/5 lead -free solder. Care should be taken not to anneal the threads. Purge with Nitrogen gas during the brazing process to prevent formation of oxides. |  | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements. Supports shall be designed for seismic zone 4.
P6 | DHW, IHW, IHWR, DHWR or SHW | Domestic Hot Water Supply or Industrial Hot Water Supply, Domestic hot water return, industrial hot water return or soft hot water | Above Ground | Seamless copper tubing (No ERW, longitudinal seam and imported piping are allowed.) | ASTM B88. NSF/ANSI 61 : Drinking Water System components - Health Effects. NSF/ANSI 372 : Drinking Water System Components – Lead-free content | Type L, hard drawn, hot temper | 1) Braze with 15% silver content "Sil-Fos" brazing alloy. 2) Provide FxF threaded unions and FxF threaded isolation valves. 3) Exposed to view at plumbing fixtures and finished equipment, satin finish CP brass pipe with threaded cast bronze fittings. 4) No soft solder allowed except within 6" of threaded couplings. | 1) Wrought copper solder sweat type, ANSI B16.22 or brass castings, ANSI B16.18 2) Press fittings as manufactured by Viega "ProPress", Mueller "Streamline" PRS, or Elkhart "Apollo Press" | Pipes up to 2": NIBCO T-585-70-66-LF Pipes 2.5": NIBCO T-585-66-LF Pipes 3"- 5": NIBCO LD3122-3 Pipes 6" and above: NIBCO LD3122-5 lug style butterfly valves. Raised full faced spiral wound gaskets and B16 studs and nuts. All components associated with potable water system shall be lead-free. Provide stem extensions on all ball valves serving isolated pipes to accommodate handle movement. Isolation valves installed higher than 10' above finished floor shall have chain operated hand wheel | Rigid Fiberglass, ASTM C335, K = 0.24 at 75F Owens Corning, Certainteed, or Johns Manville | Pipe up to 1": 1" thick fiberglass. Pipe 1.25" & above: 1.5" thick fiberglass | Exposed Indoors: ASJ + 30mil PVC Outdoors: ASJ + 0.016" Aluminum (0.032" Aluminum when subject to damage) | Yellow / Black | Run mains at evenly pitched 1 inch in 50 feet. Make allowance for expansion in all piping installation so that the usual variations in temperature (i.e. 70˚F ΔT) will not cause stress at any point. Securely anchor where necessary to distribute expansion stresses. Provide 3/4" drainage valve at low points. Anchor all lines and risers as necessary to prevent noise or vibration when water is turned on or off. Separately valve each branch and riser. Make all such valves accessible with approved type panels. Balance, vent and adjust piping to provide circulation to all fixtures and to prevent water hammer. Unions shall not be covered with insulation, and shall be readily accessible. | Braze copper pipe joints and non-threaded fittings with 15% "Sil-Fos". Threaded fittings shall be soft-soldered using 95/5 lead -free solder. Care should be taken not to anneal the threads. Purge with Nitrogen gas during the brazing process to prevent formation of oxides. |  | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements. Supports shall be designed for seismic zone 4.
P7 | DI / RO | De-ionized Water / Reverse Osmosis Water | Above Ground, in exposed non-concealed installations (e.g. above T-bar ceilings, areas without ceilings and surface mounted applications) | Stainless steel tubing, Low carbon Seamless, Grade 316L. ERW or longitudinal seamed pipes are unacceptable. | UNS-S31603 ASTM-A269 and ASME-SA213. ASTM-A312/ASME-SA312 | Stainless steel tubing with tube wall thickness of 0.035"-0.134", depending on the tube OD dimension. See remarks for wall thicknesses. | Tube fittings by Swagelok, Hy-Lok, or Caltech approved similar manufacturer. | Compression style Tube fittings similar to Swagelok, Hy-Lok, or approved equal manufacturer. | Full port ball valve, 2-piece body, blowout proof stem, 316 or 316L stainless trim & body construction, threaded ends, 1/4 turn lever handle. Conforms to MSS SP-110, as manufactured by NIBCO T-585-S6-R-66-LL | N/A | N/A | N/A | Green / White | Install a 0-125 pig Deionized water main pressure regulating valve and pressure relief valve upstream of branch distribution. Residual pressure at the DI faucet shall not exceed 25-30 pig at highest level. All components shall be compatible with De-ionized water. (i.e. stainless steel or polypropylene construction). --------------------------------------------------------------- Tube wall thickness: 1/4" OD --0.035" 3/8" OD --0.035" 1/2" OD --0.035" 3/4" OD --0.065" 1" OD --0.083" 1.25" OD --0.095" 1.5" OD --0.12" 2" OD --0.134" | Deionized water piping shall be thoroughly cleaned and be free of any oxides, oils or particulate prior to being put to service. Materials shall be pre-cleaned. Scales shall be removed through chemical de-scaling, acid pickling, and mechanical de-scaling. Degreasing and general cleaning shall be accomplished by immersion in, swabbing with, or spraying with alkaline, emulsion, chelate, acid, solvent, or detergent cleaners or a combination of these; by vapor degreasing; by ultrasonics using various cleaners; by steam, with or without a cleaner; or by high-pressure water-jetting, as outlined in ASTM-A380. DI water faucets shall be tin-lined. Poly tubing connections are unacceptable. Final connection from tubing termination to the fixture shall be made with stainless steel tubing and not poly-tubing. | Stainless steel piping system shall be chemically cleaned for a minimum of 48 hours. Pressure test piping system either hydrostatically with water as the testing medium or pnuematically with either compressed air or nitrogen as the testing medium. Pipes smaller than and equal to 2.5" diameter shall be tested using either the hydrostatic or pneumatic methods Pipes larger than 2.5" diameter shall be tested using a combination of hydrostatic and pnuematic testing using 95% water by volume and 5% compressed air to minimize any potential risks posed by stored energy in compressed air. Pipes shall be tested with a pressure of not less than 1.5 times the operating pressure but not less than 100 psig. Test pressure shall be held for a minimum period of 24 hours. Record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. Neutralize the chemicals and flush the system immediately after cleaning is completed and discharge the chemicals in accordance with the local codes and in compliance with CIT design guide. Refer to campus design guide document for the details of cleaning & passivation procedures and chemicals. | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements. Supports shall be designed for seismic zone 4.
P8 | DI / RO | De-ionized Water / Reverse Osmosis Water | Above Ground, in concealed installations (e.g. In utility chases, above hard lid ceilings and inside wall cavities) | Stainless steel pipe, Low carbon, Seamless, Grade 316L. ERW or longitudinal seamed pipes are unacceptable. | ASTM-A312/ASME-SA312 | Schedule 10S pipe | Gas Tungsten arc welding (GTAW) or Tungsten inert gas welding (TIG). Butt welded or socket welded. Mechanical fittings in concealed spaces are not acceptable. | ASTM- A312/ASME-SA312 schedule 10 seamless stainless steel butt welded. | Full port ball valve, 2-piece body, blowout proof stem, 316 or 316L stainless trim & body construction, threaded ends, 1/4 turn lever handle. Conforms to MSS SP-110, as manufactured by NIBCO T-585-S6-R-66-LL. | N/A | N/A | N/A | Green / White | Install a 0-125 pig Deionized water main pressure regulating valve and pressure relief valve upstream of branch distribution. Residual pressure at the DI faucet shall not exceed 25-30 pig. All components shall be compatible with De-ionized water. (i.e. stainless steel or polypropylene construction) |  |  | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements
P9 | W & V and SD Option #1 | Sanitary Waste & Vent (Gravity) ---------------------- Storm Drain (Gravity) | Direct Buried, Below Grade | Cast iron no-hub soil pipe to be marked with the collective trademark of Cast Iron Soil Pipe Institute (CISPI) | CISPI Standard 301 or ASTM A74, ASTM A888 and compression Gaskets comply with ASTM C564 | Standard weight | No-hub couplings to be type 304 stainless steel, FM Class 1, ASTM C1540 as manufactured by Husky "SD4000", 80 in-lb torque | DWV Standard weight cast iron no-hub fitting to be marked with the collective trademark of Cast Iron Soil Pipe Institute (CISPI) | Back water valves required to be accessible for service. [CPC 710.6] | N/A | N/A | 30 mil Polyethylene or HDPE wrap | Yellow / Black | Torque coupling bolts as per manufacturer's recommendation with a calibrated torque wrench. Caltech inspector or plumbing representative shall be present during torquing process and randomly spot check the torque settings prior to covering the work. Over-torqued couplings shall be replaced with new ones. Fixtures to drain by gravity where practicable. [CPC 709.0] When necessary due to site conditions, install sewer ejector pump per [CPC 710] Backwater valves required for fixtures below next upstream manhole cover. [CPC 710.1] Fixtures above manhole cover elevation not allowed to discharge through backwater valves (Typical). | Pipe supported on firm sand bed for entire length. [CPC 314.3] No rocks supporting or touching pipes. [CPC 315.4] Six inches of sand bed minimum for ABS/PVC drain pipe per manufacturer; no rocks or debris in first 12” of backfill over ABS pipe. [CPC 315.4] Trenches not to undermine footings within bearing plane (45˚). [CPC 315.1] Sewer and water pipe minimum 12” deep. [CPC 609.1] | Pressure test gravity piping hydrostatically with water as the testing medium at 10-foot head of water except at the highest opening. Pneumatic testing with either compressed air or nitrogen as the testing medium requires prior approval from Caltech PD&C and shall be tested at 10 psig. Test pressure shall be held for a minimum period of 4 hours. Close openings in system and fill with water and use a Bristol Gauge to record any observed leakage. Record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. Materials must be listed and all pipes must have manufactures listing and labeling. [CPC 301.1.2], Minimum slope 1/4" (2%) per foot, or when preapproved, 1/8” (1%) per foot for 4” diameter or larger. [CPC 708.0]. No reductions in pipe size allowed in direction of flow. [CPC 316.4.1]. No drilling or tapping of connections. [CPC 311.2]. Use only listed transition fittings at plastic to cast iron pipe. Minimum trap sizes per table 7-3 in the CPC. | N/A
P10 | W & V and SD Option #2 | Sanitary Waste & Vent (Gravity) ---------------------- Storm Drain (Gravity) | Direct Buried, Below Grade | PVC pipe, SDR 26 through 13.5 as needed. Pipe shall be extruded from compounds meeting the requirements of Cell Classification 12454, as defined in ASTM D1784, Standard Specification for Rigid Poly (Vinyl Chloride) (PVC) Compounds. | ASTM D3034, ASTM F679, ASTM D3212, ASTM F477, ASTM D1784, ASTM D2152, ASTM D2444 , ASTM D2321, ASTM D2412, IAPMO (File No. 2128) - Uniform Plumbing Code (UPC) - ASTM D3034 SDR 35 for pipes 4-15 inch outside diameter and SDR 26 for pipes 4-12 inch outside diameter. | Extra thick walls | The gasket shall be reinforced with a steel ring and meet the requirements of ASTM F477. Pipe shall have an integral bell end with a locked-in factory installed gasket and shall meet the requirements of ASTM D3212 Gasketed hub and spigot push type fittings conforming to ASTM D2672. Refer to plans for specific SDR rating on each project. Recommended installation procedures of PVC drain pipe are outlined in ASTM-D2321, Underground Installation of Flexible Thermoplastic Sewer Pipe. Glued joints may be allowed only after consulation with Caltech and Project manager's written approval. DWV type fittings. |  | Back water valves required to be accessible for service. [CPC 710.6] | N/A | N/A | 30 mil Polyethylene or HDPE wrap | Yellow / Black | Corrosion resistant pressure pipe, IPS sizes 3/4" through 24", for use at temperatures up to and including 140 F. Pressure rating (100 psi to 200 psi) varies with SDR Series and temperature ratings. Typical applications include: Sanitary sewer waste & vent, Grease interceptor waste, storm water drain and sub-soil site drainage. Fixtures to drain by gravity where practicable. [CPC 709.0] When necessary due to site conditions, backwater valves required for fixtures below next upstream manhole cover. [CPC 710.1] Fixtures above manhole cover elevation not allowed to discharge through backwater valves (Typical). | Pipe supported on firm sand bed for entire length. [CPC 314.3] No rocks supporting or touching pipes. [CPC 315.4] Six inches of sand bed minimum for ABS/PVC drain pipe per manufacturer; no rocks or debris in first 12” of backfill over ABS pipe. [CPC 315.4], Trenches not to undermine footings within bearing plane (45˚). [CPC 315.1] Sewer and water pipe minimum 12” deep. [CPC 609.1] |  | N/A
P10A | Kitchen grease W & V | Kitchen grease Waste & Vent (Gravity) | Direct Buried, Below Grade and above ground | Extra heavy Cast iron no-hub soil pipe to be marked with the collective trademark of Cast Iron Soil Pipe Institute (CISPI) | CISPI Standard 301 or ASTM A74 and compression Gaskets comply with ASTM C564 | Extra thick walls weight | No-hub couplings to be type 304 stainless steel, FM Class 1, ASTM C1540 as manufactured by Husky "SD4000", 80 in-lb torque | Standard weight cast iron no-hub fitting to be marked with the collective trademark of Cast Iron Soil Pipe Institute (CISPI) | Back water valves required to be accessible for service. [CPC 710.6] | N/A | N/A | 30 mil Polyethylene or HDPE wrap | Yellow / Black | Torque coupling bolts as per manufacturer's recommendation with a calibrated torque wrench. Caltech inspector or plumbing representative shall be present during torquing process and randomly spot check the torque settings prior to covering the work. Over-torqued couplings shall be replaced with new ones. Fixtures to drain by gravity where practicable. [CPC 709.0] When necessary due to site conditions, install sewer ejector pump per [CPC 710] Backwater valves required for fixtures below next upstream manhole cover. [CPC 710.1] Fixtures above manhole cover elevation not allowed to discharge through backwater valves (Typical). | Direct-buried pipe shall be supported on firm sand bed for entire length. [CPC 314.3] No rocks supporting or touching pipes. [CPC 315.4] Six inches of sand bed minimum for ABS/PVC drain pipe per manufacturer; no rocks or debris in first 12” of backfill over ABS pipe. [CPC 315.4] Trenches not to undermine footings within bearing plane (45˚). [CPC 315.1] Sewer and water pipe minimum 12” deep. [CPC 609.1] |  | N/A
P11 | IW, CD, OCD, V | Indirect waste, Equipment Cold Drains,Overflows Condensate Drains, & Vents | Above Ground | Domestic (US Made) seamless copper tubing (No ERW, longitudinal seam and imported piping are allowed.) | ASTM B88 | Type L, Hard drawn | 1) Braze with 15% silver content "Sil-Fos" brazing alloy. 2) Provide FxF threaded unions and FxF threaded isolation valves. | 1) ANSI / ASME B16.22, Solder wrought copper 2) Press fittings as manufactured by Viega "ProPress", Mueller "Streamline" PRS, or Elkhart "Apollo Press" | N/A | Elastomeric, ASTM C534 Type I, ASTM C177, K = 0.27 at 75F "ArmaFlex" by Armacell Air vent pipes do not need to be insulated | 0.5" thick elastomeric | Exposed Indoors: ASJ + 30mil PVC / Outdoors: ASJ + 0.016" Aluminum (0.032" Aluminum when subject to damage) | Green / White with arrows in the direction of flow | Steam vent pipes need to be insulated. Air Vent Pipes do not need to be insulated. | No soft solder allowed except within 6" of threaded couplings. | Copper piping system shall be chemically cleaned for a minimum of 48 hours. Pressure test piping system either hydrostatically with water as the testing medium or pnuematically with either compressed air or nitrogen as the testing medium. Pipes smaller than and equal to 2.5" diameter shall be tested using either the hydrostatic or pneumatic methods Pipes larger than 2.5" diameter shall be tested using a combination of hydrostatic and pnuematic testing using 95% water by volume and 5% compressed air to minimize any potential risks posed by stored energy in compressed air. Pipes shall be tested with a pressure of not less than 1.5 times the operating pressure but not less than 100 psig. Test pressure shall be held for a minimum period of 24 hours. Record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. Neutralize the chemicals and flush the system immediately after cleaning is completed and discharge the chemicals in accordance with the local codes and in compliance with CIT design guide. Refer to campus design guide document foot the details of cleaning & passivation procedures and chemicals. | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements
P12 | W & V | Sanitary Waste & Vent | Above Ground | Cast iron no-hub soil pipe to be marked with the collective trademark of Cast Iron Soil Pipe Institute (CISPI) | CISPI Standard 301 or ASTM A74, ASTM A888 and compression Gaskets comply with ASTM C564 | Standard weight | No-hub couplings to be type 304 stainless steel, FM Class 1, ASTM C1540 as manufactured by Husky "HD2000", 60 in-lb torque. | Standard weight cast iron no-hub fitting to be marked with the collective trademark of Cast Iron Soil Pipe Institute. DWV type fittings | same as above | N/A | N/A | N/A | Yellow / Black | Same as above | N/A | N/A | N/A
P13 | SSD | Sub-Surface or Foundation Drain | Embedded / Direct Buried Sub-Surface | PVC pipe, perforated, Class 12454-B (PVC 1120), ASTM D2729; primer, ASTM F656; solvent cement, ASTM 2564; with polypropylene fabric filter cover. | Class 12454-B (PVC 1120), ASTM D2729 | PVC, Schedule 40 | Solvent cement chemical adhesive | PVC fittings, perforated, Class 12454-B (PVC 1120), ASTM D2729 Primer, ASTM F656 Solvent cement, ASTM 2564 Provide with polypropylene fabric filter cover | N/A | N/A | N/A | N/A | Green / White | Pipe supported on firm bed for entire length. [CPC 314.3] No rocks supporting or touching pipes. [CPC 315.4] Six inches of sand bed minimum for ABS/PVC drain pipe per manufacturer; no rocks or debris in first 12” of backfill over ABS pipe. [CPC 315.4] Trenches not to undermine footings within bearing plane (45˚). [CPC 315.1] Sewer and water pipe minimum 12” deep. [CPC 609.1] |  | Pressure test gravity piping hydrostatically with water as the testing medium at 10-foot head of water except at the highest opening. Pneumatic testing with either compressed air or nitrogen as the testing medium requires prior approval from Caltech PD&C and shall be tested at 10 psig. Test pressure shall be held for a minimum period of 4 hours. Close openings in system and fill with water and use a Bristol Gauge to record any observed leakage. | N/A
P14 | PSE | Pumped Sewage Ejector/ Pumped Storm Drain and Sump Pump Discharge Piping and Fittings | Direct Buried, Pumped Discharge Piping Below Ground | Type K, Hard Drawn Copper Pipe | ASTM B88 | Rigid | 1) Braze with 15% silver content "Sil-Fos" brazing alloy. 2) Provide FxF threaded unions and FxF threaded isolation valves. | 1) Wrought copper solder sweat type, ANSI B16.22 or brass castings, ANSI B16.18. 2) DWV type fittings 3) Press fittings as manufactured by Viega "ProPress", Mueller "Streamline" PRS, or Elkhart "Apollo Press" | Option 1: Rising stem full ported cast iron gate valve, class 250, ASME B 16.4; ASME B16.12; ASTM A 74; ASTM A 888; CISPI 301. Option 2: Pipes 3"- 5": NIBCO LD3122-3 Pipes 6" and above: NIBCO LD3122-5 lug style butterfly valves. Raised full faced spiral wound gaskets and B16 studs and nuts. Isolation valves installed higher than 10' above finished floor shall have chain operated hand wheel. | N/A | N/A | 8 mil polyethylene jacketing, fluorescent green color | Yellow / Black | Piping includes all discharge piping from pumps to a point of connection where pump discharge connects to gravity drainage line. No hub couplings are not acceptable on any pumped discharge line. | Install NIBCO "NHE300F" or "F-918-B" check valve on the discharge pipe (exact size to be determined by plumbing engineer) | Pressure test piping system either hydrostatically with water as the testing medium or pnuematically with either compressed air or nitrogen as the testing medium. Pipes smaller than and equal to 2.5" diameter shall be tested using either the hydrostatic or pneumatic methods Pipes larger than 2.5" diameter shall be tested using a combination of hydrostatic and pnuematic testing using 95% water by volume and 5% compressed air to minimize any potential risks posed by stored energy in compressed air. Pipes shall be tested with a pressure of not less than 1.5 times the operating pressure but not less than 100 psig. Test pressure shall be held for a minimum period of 4 hours using a Bristol Gauge to record any observed leakage. | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements. Supports shall be designed for seismic zone 4.
P15 | PSE | Pumped Sewage Ejector/ Pumped Storm Drain and Sump Pump Discharge Piping and Fittings | Pumped Discharge Piping Above Ground | Hot dipped galvanized seamless carbon steel pipe, domestic made with grooved ends with Victaulic style couplings or screwed ends. | ASTM A-53S, grade A or B | Schedule 40 | <2" - Screwed On >2" - Mechanical / Grooved style couplings | Galvanized Victaulic couplings are acceptable. "No-hub" type couplings are prohibited for this application. |  | N/A | N/A | N/A | Yellow / Black | Piping includes all discharge piping with earthquake strap from units to a point of connection where pump discharge connects to gravity drainage line. No hub couplings are not acceptable on any pumped discharge line. | Install NIBCO "NHE300F" or "F-918-B" check valve on the discharge pipe (exact size to be determined by plumbing engineer) |  | N/A
P16 | SD & OD | Storm Drainage and Roof Drain Pipe and Pipe Fittings | Direct Buried, Below Grade | Cast iron no-hub soil pipe to be marked with the collective trademark of Cast Iron Soil Pipe Institute | CISPI Standard 301 or ASTM A74 | Service weight | Couplings shall conform to requirements of ASTM C1540, FM 1680. Heavy duty type 304 stainless steel shielded couplings with a 28 Gauge shield, Husky "SD4000" or equal. | ASTM A 74-13A ASTM A 888 DWV type fittings | N/A | N/A | N/A | 30 mil Polyethylene or HDPE wrap | Green / White | Alternate Material, where applicable and subject to approval by local authorities having jurisdictions. 1) Piping shall be PVC DWV conforming to ASTM D2665-2004A. 2) Fittings shall be PVC DWV conforming to ASTM 3311-2002. |  | Pressure test gravity piping hydrostatically with water as the testing medium at 10-foot head of water except at the highest opening. Pneumatic testing with either compressed air or nitrogen as the testing medium requires prior approval from Caltech PD&C and shall be tested at 10 psig. Test pressure shall be held for a minimum period of 4 hours. Close openings in system and fill with water and use a Bristol Gauge to record any observed leakage. | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements. Supports shall be designed for seismic zone 4.
P17 | SD & OD | Storm Drainage and Roof Drain Pipe and Pipe Fittings | Above Ground | Cast iron no-hub soil pipe to be marked with the collective trademark of Cast Iron Soil Pipe Institute | CISPI Standard 301 or ASTM A74 | Standard weight | No-hub couplings to be type 304 stainless steel, FM Class 1, ASTM C1540 as manufactured by Husky "SD2000" or "Clamp-All 125" | ASTM A 74-13A ASTM A 888 DWV type fittings | N/A | Elastomeric, ASTM C534 Type I, ASTM C177, K = 0.27 at 75F "ArmaFlex" by Armacell | N/A | N/A | Green / White | Closed cell insulation shall be provided for all storm and overflow drain piping subject to condensation. |  |  | N/A
P18 | FW Option #1 | Combined Fire protection & potable water Pipe and Pipe Fittings | Direct Buried, Below Grade | Pipes 3" & above: Cement-lined and seal coated ductile iron, Class 53 or 54 with polyethylene encasement, asphaltic coated or wrapped class 54 on the outside. | Cement lined ductile iron pipe. ANSI / AWWA C/104, C151 / A21.51, C150 / A21.50, C111 / A21.11 | Ductile iron, | Mechanical joints, "MEGALUG series 1100 TDM" or "MEGALUG series 1700" as appropriate for the application and joint type. | Provide ductile iron fittings conforming to AWWA C110 with a minimum rated working pressure of 350 psi. Provide fittings with bells and gaskets specifically designed for cast iron equivalent outside diameter PVC pipe. Use mechanical joint fittings or fittings with bells and gasket ends. | Listed fire protection valves, UL, ULC, FM global, and fire marshal listed and approved. See design guide for additional requirements. | N/A | N/A |  | Red / White | Install concrete anchor thrust blocks or tie-rods on all underground lines at all tees and elbows to prevent movement when under pressure. All tie-rods, clamps, brackets, and bolts shall be ductile iron, stainless steel, galvanized or epoxy coated. Flanged restraints shall be similar to "MEGALUG series 1100" or "MEGALUG 1700 series". Sterilize water system by introducing chlorinating solution into the entire system for a minimum period of 24 hours. Maintain concentration of 50-150 ppm. Residual chlorine not to exceed 0.2 ppm. (See pipe specification in Division 21 in the Caltech Design Guidelines) | Pipe supported on firm sand bed for entire length. [CPC 314.3] No rocks supporting or touching pipes. [CPC 315.4] Six inches of sand bed minimum for ABS/PVC drain pipe per manufacturer; no rocks or debris in first 12” of backfill over ABS pipe. [CPC 315.4] Trenches not to undermine footings within bearing plane (45˚). [CPC 315.1] Sewer and water pipe to be buried minimum 18” deep. [CPC 609.1] | Testing shall be in accordance with NFPA standards, upon completion prior to acceptance of the installation subject the system to a hydrostatic pressure test with no visible leakage. Remove and replace all defects due to materials or workmanship occurring during the test and retest after corrections have been made. All testing shall be approved by Caltech and FM Global representatives and City of Pasadena Fire Inspector. The contractor shall complete two sets of FM Global's contractors material and test certificate for underground piping. One set is for Caltech's permanent records, and one is for FM global. | N/A
P19 | FW Option #2 | Combined Fire protection & potable water Pipe and Pipe Fittings | Direct Buried, Below Grade | Pipes 4" & above: AWWA C900 PVC pipe, DR18 / 200 PSI pressure class | Material Cell Classification 12454-8 per ASTM D 1784 | PVC | Provide polyvinyl chloride (PVC) couplings with twin elastomeric gaskets / retaining glands which are designed to connect straight ends of plain pipe and allow 2 degrees of deflection at each gasket for a total of 4 degrees per coupling. | Ductile iron fittings or AWWA-C900 PVC | Listed fire protection valves, UL, ULC, FM global, and fire marshal listed and approved. See design guide for additional requirements. | N/A | N/A |  | Red / White | Install concrete anchor thrust blocks or tie-rods on all underground lines at all tees and elbows to prevent movement when under pressure. All tie-rods, clamps, brackets, and bolts shall be ductile iron, stainless steel, galvanized or epoxy coated. Flanged restraints shall be similar to "MEGALUG series 1100" or "MEGALUG 1700 series". Sterilize water system by introducing chlorinating solution into the entire system for a minimum period of 24 hours. Maintain concentration of 50-150 ppm. Residual chlorine not to exceed 0.2 ppm. | Schedule 10 or plastic pipe is not allowed. Provide carbon steel schedule 40 ASTM. A-795 pipe with roll-grooved pipe or welded joints |  | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements
P20 | FW/FS | Dedicated Fire sprinkler Pipe and Pipe Fittings | Above Ground and inside the building | Schedule 40 seamless carbon steel pipe with threaded, welded or cut grooved joints for sizes 2" and below. Mains may be flexible or rigid grooved couplings. Pipe 3" and over can be mechanical flexible grooved couplings. No Schedule 10 ASTM A-795 black steel pipe with roll-grooved or welded joints are allowed. | ASTM A-53S, grade A or B, seamless, Domestic made | Schedule 40 | Welded joints shall be made using factory-fabricated steel welding fittings. Grooved end malleable iron fittings and bolted clamp type malleable iron couplings with rubber sealing gaskets for grooved end pipe with appropriate pressure rating, similar to Victaulic Style 75 may be used, except on dry pipe and/or pre-action systems. Couplings shall be provided with rubber "flush seal" gaskets of the same manufacturer as the coupling and intended to be used together. | Standard weight carbon steel, butt weld ASTM B16.3. | Listed fire protection valves, UL, ULC, FM global, and fire marshal listed and approved. See design guide for additional requirements. Isolation valves installed higher than 10' above finished floor shall have chain operated hand wheel. | N/A | N/A | N/A | Red / White | All expansion joint fittings shall be FM approved. Provide ground joint type unions for 2 inch and smaller pipe, of galvanized iron with brass seats. Black and hot-dipped Zinc coated (Galvanized) welded and seamless steel pipe, ASTM A795: 1) Between Siamese and check valve, ball drip drains, drain and test piping subject to alternate wetting and drying, test and relief piping, water motor gong piping, and normal dry piping. 2) Fittings and couplings for galvanized pipes shall be galvanized. 3) Provide anti-microbial internal coating protection for all pipes. | Clean and flush pipes after installation | 1) Pressure test the piping system with compressed air for a minimum of 24 hours at 150 psi using a Bristol Gauge.. 2) Pressure test shall be observed by a Caltech inspection representative and signed off in writing. 3) Testing shall be in accordance with NFPA standards upon completion of the installation and prior to acceptance of the installation. 4) Remove and replace all defects due to materials or workmanship occurring during the test and retest after corrections have been made. 5) All testing shall be approved by Caltech and FM Global representatives and City of Pasadena Fire Inspector. 6) The contractor shall complete two sets of FM Global's contractors material and test certificate for above ground piping. One set for Caltech's permanent records, and one set is for FM global. | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements. Supports shall be designed for seismic zone 4.
P21 | HPA, AIR & VAC | Nitrogen, High Pressure Compressed Air, Low pressure Compressed Air and Vacuum | Above Ground | Oxy-Med grade Type L, hard drawn seamless copper tubing, cleaned, nitrogen charged & capped at the factory similar to "CerroPure" | ASTM B819 --- OXYMED ASTM B280 ---- ACR tubing | OXY-MED grade Type L, hard drawn | 1) Braze with 15% silver content "Sil-Fos" brazing alloy. 2) Provide FxF threaded unions and FxF threaded isolation valves. 3) Press fittings are acceptable only with Caltech's permission | Wrought copper solder sweat type, ANSI B16.22 or brass castings, ANSI B16.18. Fittings shall be sealed and bagged to maintain cleanliness prior to installation. (i.e. similar to OXY-MED or ACR) | Valves shall be sealed and bagged to maintain cleanliness prior to installation. -------------------------------------------------------------------------- Pipes up to 2": NIBCO T-585-70-66-LF Pipes 2.5": NIBCO T-585-66 Pipes 3"- 5": NIBCO LD3122-3 with raised full faced spiral wound gaskets and B16 studs and nuts. | N/A | N/A | N/A | Nitrogen ---Yellow/Black HPA ---Yellow/Black, AIR --- Blue/White, Vacuum ---Yellow/Black SG --- Yellow/Black | Copper tubing shall be charged with nitrogen at the factory and sealed on both ends when delivered to the job site to ensure against any contamination. Install 5 micron particulate filters and/or refrigerated air dryer serving compressed air (i.e. CA and HPA) to the labs, as per lab programmers instructions on plans and specifications. | Braze copper pipe joints and non-threaded fittings with 15% "Sil-Fos". Threaded fittings shall be soft-soldered using 95/5 lead -free solder. Care should be taken not to anneal the threads. Purge with Nitrogen gas during the brazing process to prevent formation of oxides. | 1) Pressure test steel piping system with compressed nitrogen for a minimum of 24 hours at 1.5 times maximum working pressure or 150 PSI minimum. 2) Pressure test shall be observed by a Caltech inspection representative and signed off in writing. 3) Fittings for pressed joints shall be cleaned and bagged separately off-site and delivered to the jobsite free of particulates and contamination. 4) Pressures readings shall be recorded using a Bristol gauge | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements. Supports shall be designed for seismic zone 4.
P22 | SG (non-reactive and blended non-reactive gases) | Special lab gases: inert and non-reactive and blended non-reactive (e.g. Carbon dioxide, nitrogen, argon, helium) | Above Ground | Oxy-Med, Type L, hard drawn seamless copper tubing, cleaned & capped | ASTM B819 | Type L, hard drawn | 1) Braze with 15% silver content "Sil-Fos" brazing alloy. 2) Provide FxF threaded unions and FxF threaded isolation valves. 3) Piping serving helium shall be brazed; no exceptions whatsoever. | Wrought copper solder sweat type, ANSI B16.22 or brass castings, ANSI B16.18. Fittings shall be sealed and bagged to maintain cleanliness prior to installation (i.e. similar to OXY-MED or ACR) Press fittings as manufactured by Viega "ProPress", Mueller "Streamline" PRS, or Elkhart "Apollo Press" | Pipe up to 2.5": NIBCO T685-66 or NIBCO T-585-66 ball valves Pipes 3"- 5": NIBCO LD3122-3. Pipes 6" and above: NIBCO LD3122-5 lug style butterfly valves. Raised full faced spiral wound gaskets and B16 studs and nuts. Valves shall be sealed and bagged to maintain cleanliness prior to installation. | N/A | N/A | N/A | Yellow/Black | Piping shall be nitrogen charged, capped and sealed during installation and kept free of contaminants | Braze copper pipe joints and non-threaded fittings with 15% "Sil-Fos". Threaded fittings shall be soft-soldered using 95/5 lead -free solder. Care should be taken not to anneal the threads. Purge with Nitrogen gas during the brazing process to prevent formation of oxides. | 1) Pressure test steel piping system with compressed nitrogen for a minimum of 24 hours at 1.5 times maximum working pressure or 150 PSI minimum. 2) Pressure test shall be observed by a Caltech inspection representative and signed off in writing. 3) fittings for pressed joints shall be cleaned and bagged separately off-site and delivered to the jobsite free of particulates and contamination. 4) pressures readings shall be recorded using a Bristol gauge | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements. Supports shall be designed for seismic zone 4.
P23 | SG (hazardous and toxic gases) | General Lab Gases | Above Ground | Stainless steel tubing | ASTM A269 TP316L, seamless, fully annealed | seamless 316L | Swagelok tube fitting, or approved equal by Hy-Lok | Swagelok "VCR", or approved equal by Hy-Lok | Swagelok ball valve, or approved equal by Hy-Lok | N/A | N/A | N/A | Red / White | Piping shall be cleaned, capped, and sealed prior to delivery to installation and kept free of contaminants | All joints shall be mechanically connected (no soldering or brazing permitted). System shall be cleaned and capped prior to delivery to the project site. Perform pressure test with nitrogen and helium leak test prior to commissioning. | 1) Pressure test steel piping system with compressed nitrogen for a minimum of 24 hours at 1.5 times maximum working pressure or 150 PSI minimum. 2) Pressure test shall be observed by a Caltech inspection representative and signed off in writing. 3) Fittings for pressed joints shall be cleaned and bagged separately off-site and delivered to the jobsite free of particulates and contamination. 4) Pressures readings shall be recorded using a Bristol gauge | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements. Supports shall be designed for seismic zone 4.
P24 | SG (combustible and/pr explosive gases) | combustible and/or explosive (e.g. hydrogen H2) | Above Ground | Stainless steel tubing | ASTM A269 TP316L, seamless, fully annealed | seamless 316L | Swagelok tube fitting, or approved equal by Hy-Lok | Swagelok "VCR", or approved equal by Hy-Lok | Swagelok ball valve, or approved equal by Hy-Lok | N/A | N/A | N/A | Red / White | Piping shall be cleaned, capped, and sealed prior to delivery to installation and kept free of contaminants | All joints shall be mechanically connected (No soldering or brazing permitted). System shall be cleaned and capped prior to delivery to the project site. Perform pressure test with nitrogen and helium leak test prior to commissioning. | 1) Pressure test steel piping system with compressed nitrogen for a minimum of 24 hours at 1.5 times maximum working pressure or 150 PSI minimum. 2) Pressure test shall be observed by a Caltech inspection representative and signed off in writing. 3) Fittings for pressed joints shall be cleaned and bagged separately off-site and delivered to the jobsite free of particulates and contamination. 4) Pressures readings shall be recorded using a Bristol gauge | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements. Supports shall be designed for seismic zone 4.
P25 | LG | High Purity and ultra-high purity, corrosive or toxic gases: (e.g. Carbon dioxide, nitrogen, argon, helium, Ammonia, HF, etc.) | Above Ground | Stainless Steel tubing (No ERW, longitudinal seam and imported piping are allowed.) | Only tubing made in USA, Japan or Germany shall be acceptable | Stainless Steel SS316L, minimum wall thickness: 0.035"-0.095" for low pressure side of distribution | Compression style for all applications unless specifically called out to be orbital welded with VCR type gaskets | Tube type fittings similar to Swagelok, Hy-Lok or approved equal. | Swagelok "40 Series" or "60 Series", Hy-Lok "105 Series" ball valves, unless specified otherwise by the lab planner, project specification book or construction drawings. | N/A | N/A | N/A | Yellow / Black | Piping shall remain sealed during installation and kept free of contaminants Tubing for ultra-high purity gases my need to be electro-polished as per lab programming requirements. |  | 1) Pressure test steel piping system with compressed nitrogen for a minimum of 24 hours at 1.5 times maximum working pressure or 150 PSI minimum. 2) Pressure test shall be observed by a Caltech inspection representative and signed off in writing. 3) Fittings for pressed joints shall be cleaned and bagged separately off-site and delivered to the jobsite free of particulates and contamination. 4) Pressures readings shall be recorded using a Bristol gauge. | N/A
P26 | AW & AV | Acid Waste & Acid Vent with liquids at elevated temperatures only when required and approved by Caltech (Gravity) | Direct buried, Below Grade only | Corrosion resistant cast iron drainage piping to be marked with collective trademark of Cast Iron Soil Pipe Institute (CISPI) | ASTM A518, ASTM A861 | DURIRON "MJ series" | DURIRON "MJ series" mechanical joint consists of an inner sleeve of PTFE, surrounded by an outer sleeve of Neoprene rubber, with two sleeves are held in place by a 300 series stainless steel coupling. The two bolt coupling is resistant to corrosion by organic and inorganic acids and their salts | DURIRON corrosion resisting cast iron fitting to be marked with the collective trademark of Cast Iron Soil Pipe Institute. (CISPI) The mechanical joint coupling shall consist of an inner sleeve of PTFE, an outer sleeve of Neoprene rubber (a product of The DuPont DeNemours Company), and an outer band of 300-series stainless steel. Mechanical joint couplings shall be installed by alternately tightening the nuts to a minimum of 9 ft-lbs. and a maximum of 11 ft-lbs. torque. | N/A | N/A | N/A | N/A | Yellow / Black | For systems being installed underground, a trench shall be excavated so as to provide adequate room to make joints, align, and grade the pipe. The trench bottom shall be properly compacted and rock-free and shall support the pipe throughout its entire length. Fill material shall be applied in layers not exceeding 6 inches loose depth and each layer shall be thoroughly compacted. The first 6 inches of fill material shall be rock-free. The system shall be installed and tested in accordance with the manufacturer’s instructions and all governing plumbing codes. | Apply 3 coats of asphaltic coating on the joins. Mechanical type joints & fittings shall not be allowed for installation in concealed spaces and shafts. | Pressure test gravity piping hydrostatically with water as the testing medium at 10-foot head of water except at the highest opening. Pneumatic testing with either compressed air or nitrogen as the testing medium requires prior approval from Caltech PD&C and shall be tested at 10 psig. Test pressure shall be held for a minimum period of 4 hours. Close openings in system and fill with water and use a Bristol Gauge to record any observed leakage. Record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements. Supports shall be designed for seismic zone 4.
P27 | AW & AV | Acid Waste & Acid Vent with liquids at elevated temperatures only when required and approved by Caltech (gravity) | Direct buried, Below Grade or above ground in non-concealed spaces (only with Caltech's approval) | Austenitic 316L Stainless steel pipe with 16.5%-18.5% chromium content | ASME A112.3.11, IAPMO file # 3247, City of LA | JOSAM 316L stainless steel | Push-fit with lip-sealing ring joint. Purple sealing ring made from fluorine rubber (Viton®). Heat-resistant and resistant to oil, solvents and strong acids. Type of sealing ring shall be compatible with the chemical exposure & resistant list | Matching Blucher push-fit connection system. Stainless steel AISI304 / EN 1.4301 or AISI316L/ EN 1.4404 | N/A | N/A | N/A | N/A | Yellow / Black | FPM seal has only limited resistance to e.g. butyl acetate, acetone and methyl alcohol. Exact type of seal to be selected during lab programming and design. (e.g. EPDM, NBR or FPM). Load Ratings are based upon maximum anticipated traffic, in accordance with American National Standards ASME A112.21.1M. --- Light Duty (LD): Safe Live Load Under 2000 lbs. --- Medium Duty (MD): Safe Live Load 2000-4999 lbs. --- Heavy Duty (HD): Safe Live Load 5000-7499 lbs. --- Extra Heavy Duty (XHD): Safe Live Load Between 7500 and 10,000 lbs. --- Special Duty (SD): Safe Live Load Over 10,000 lbs. | Follow recommended manufacturer's installation procedure. Mechanical type joints & fittings shall not be allowed for installation in concealed spaces and shafts. | Pressure test gravity piping hydrostatically with water as the testing medium at 10-foot head of water except at the highest opening. Pneumatic testing with either compressed air or nitrogen as the testing medium requires prior approval from Caltech PD&C and shall be tested at 10 psig. Test pressure shall be held for a minimum period of 4 hours. Close openings in system and fill with water and use a Bristol Gauge to record any observed leakage. Record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements. Supports shall be designed for seismic zone 4.
P28 | AW & AV See note 1 below | Acid Waste & Acid Vent (gravity) | Above Ground, Inside wall cavities and concealed shaft spaces. | Corrosion / Chemical resistant flame retardant polypropylene drainage piping | ASTM D635, ASTM D4101 | IPEX "Enfield" Schedule 40 polypropylene | IPEX "Enfield's" Electrofusion joints --- Fusion cycle controlled by the latest microprocessor operated, waterproof, Enfusion control unit. The unit shall be capable of fusing multiple joints and with a minimum capability of eight 2" joints with the same fusion time as a single joint. Connections between polypropylene and other piping materials shall be made using Enfield adapters according to manufacturer’s (IPEX) recommendations. All electrofusion machines shall be third party certified by UL and CSA. | IPEX "Enfield's" electrofusion fittings shall be NSF listed and have an integral heavy gauge, nickel/chrome electrical resistance wire molded in place in the fitting body. Copper wire elements, loose wire or other loose joint components, are prohibited. Fittings shall be IPEX "Enfield" or approved equal. | N/A | N/A | N/A | N/A | Yellow / Black | Installation and testing shall be in accordance with the contract drawings, the manufacturer’s recommendations and the local plumbing codes. Testing with compressed air is prohibited. The entire system shall be installed free of stress and in proper alignment. Horizontal supports shall provide a wide bearing area and be free of burrs or sharp edges. Support spacings shall be in accordance with the manufacturer’s recommendations and local plumbing codes. Vertical piping shall have riser clamps at each floor. Pipe supports should be installed so that horizontal piping is in uniform alignment and with a uniform slope of at least 1/8" (1%). | Install IPEX "Enfield" with electrofusion joint, unless noted in all location expect for Plenumline or Labline required, see comments below. | Pressure test gravity piping hydrostatically with water as the testing medium at 10-foot head of water except at the highest opening. Pneumatic testing with either compressed air or nitrogen as the testing medium requires prior approval from Caltech PD&C and shall be tested at 10 psig. Test pressure shall be held for a minimum period of 4 hours. Close openings in system and fill with water and use a Bristol Gauge to record any observed leakage. Record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements. Supports shall be designed for seismic zone 4.
P29 | AW & AV | Acid Waste & Acid Vent (gravity) | Above Ground, inside active return air plenums in visible and accessible spaces only | Made from "Kynar 740-02", Flame Retardant Polyvinylidene Fluoride (FR-PVDF) piping. Schedule 40, as manufactured by IPEX | Kynar "740-02", ASTM F1673, ASTM E84 and UL 723, | IPEX "Plenumline" Schedule 40 FR-PVDF | IPEX "Plenumline" mechanical joint system. Joints shall utilize factory-manufactured gasketed socket or coupling assemblies with elastomeric seals compatible with acid waste service. Solvent cementing or field fusion is not permitted. Installation shall be in accordance with manufacturer’s published instructions. Mechanical joints shall not be installed in concealed spaces unless accessible. | IPEX "Plenumline" pipe and fittings shall be ASTM F1673 standard specification for polyvinylidene Fluoride (FR-PVDF) corrosive waste drainage systems. Material used in the manufacturing of IPEX "Plenumline" pipe and fittings complied with the material requirements of ASTM D3222 standard specification for unmodified polyvinylidene Fluoride (PVDF) Molding Extrusion and Coating Materials. All pipe and fittings are listed to NSF14 standards and are IAPMO fully listed. Plenumline pipe and fittings shall have a flame spread index (FSI) of 5 and a smoke development (SDI) of 35 as tested in accordance with ASTM E84 (UL 723) and the material is UL listed. | N/A | N/A | N/A | N/A | Yellow / Black | Installation and testing shall be in accordance with the contract drawings, the manufacturer’s recommendations and the local plumbing codes. Testing with compressed air, including air booster over water, is prohibited. The entire system shall be installed free of stress and in proper alignment. Horizontal supports shall provide a wide bearing area and be free of burrs or sharp edges. Support spacings shall be in accordance with the manufacturer’s recommendations and local plumbing codes. Vertical piping shall have riser clamps at each floor. Pipe supports shall be installed so that horizontal piping is in uniform alignment and with a uniform slope of at least 1/8” per foot (1%), or in accordance with the local plumbing code requirements. Piping system is only intended for gravity lab waste and vent system and not a forced pumped system. Mechanical type joints & fittings shall not be allowed for installation in concealed spaces and shafts. | Install IPEX "Plenumline" in active air plenums where Flame Spread Index (FSI) and Smoke Developed Index (SDI) require the installation of FR-PVDF material. | Pressure test gravity piping hydrostatically with water as the testing medium at 10-foot head of water except at the highest opening. Pneumatic testing with either compressed air or nitrogen as the testing medium requires prior approval from Caltech PD&C and shall be tested at 10 psig. Test pressure shall be held for a minimum period of 4 hours. Close openings in system and fill with water and use a Bristol Gauge to record any observed leakage. Record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements
P30 | AW & AV See note 1 below | Acid Waste & Acid Vent (gravity) | Above Ground, inside wall cavities and concealed shaft spaces. | Corrosion / Chemical resistant flame retardant polypropylene drainage piping | ASTM D635, ASTM D4101 | IPEX "Labline" Schedule 40 polypropylene | IPEX "Labline" mechanical joint system. Joints shall utilize manufacturer’s gasketed coupling or socket connections with elastomeric seals suitable for acid waste service. Solvent cementing is not permitted. Installation shall comply with manufacturer’s published instructions. Mechanical joints shall not be installed in inaccessible concealed spaces or shafts. | IPEX "Labline" polypropylene drainage fittings conforming to ASTM D4101 and ASTM D635. Fittings shall be injection molded, Schedule 40, chemical-resistant polypropylene compatible with LabLine pipe. Mechanical joint fittings shall utilize manufacturer’s proprietary gasketed coupling system. All fittings shall be UL listed for flame spread (FSI 25 or less) and smoke development (SDI 50 or less) where installed in plenum or concealed spaces, in accordance with ASTM E84 (UL 723). Fittings shall be IPEX or approved equal. | N/A | N/A | N/A | N/A | Yellow / Black | Installation and testing shall be in accordance with the contract drawings, the manufacturer’s recommendations and the local plumbing codes. Testing with compressed air is prohibited. The entire system shall be installed free of stress and in proper alignment. Horizontal supports shall provide a wide bearing area and be free of burrs or sharp edges. Support spacings shall be in accordance with the manufacturer’s recommendations and local plumbing codes. Vertical piping shall have riser clamps at each floor. Pipe supports should be installed so that horizontal piping is in uniform alignment and with a uniform slope of at least 1/8" (1%). | Install IPEX "Labline" in non-plenum areas only. | Pressure test gravity piping hydrostatically with water as the testing medium at 10-foot head of water except at the highest opening. Pneumatic testing with either compressed air or nitrogen as the testing medium requires prior approval from Caltech PD&C and shall be tested at 10 psig. Test pressure shall be held for a minimum period of 4 hours. Close openings in system and fill with water and use a Bristol Gauge to record any observed leakage. Record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements. Supports shall be designed for seismic zone 4.
P31 | PAW | Pumped Acid Waste | Direct buried pumped Discharge acid waste piping | Seamless Schedule 40 Stainless Steel Pipe Grade 316L. ERW or longitudinal seamed pipes are unacceptable. | ASTM-A312 / ASME-SA312 | Schedule 40S | Gas Tungsten arc welding (GTAW) or Tungsten inert gas welding (TIG) | ASTM- A312/ASME-SA312 schedule 40 seamless stainless steel butt welded. When required, install only long radius elbows. | Pipes up to 2": class 300 psi stainless steel gate valve, Pipes 2.5" and above: class 150 psi rising stem stainless steel gate valves. Make and model # to be approved by Caltech | N/A | N/A | N/A | Yellow / Black | Piping shall be suitable for a minimum working pressure of 250 PSIG. |  | Pressure test piping system either hydrostatically with water as the testing medium or pnuematically with either compressed air or nitrogen as the testing medium. Pipes smaller than and equal to 2.5" diameter shall be tested using either the hydrostatic or pneumatic methods Pipes larger than 2.5" diameter shall be tested using a combination of hydrostatic and pnuematic testing using 95% water by volume and 5% compressed air to minimize any potential risks posed by stored energy in compressed air. Pipes shall be tested with a pressure of not less than 1.5 times the operating pressure but not less than 100 psig. Test pressure shall be held for a minimum period of 4 hours; use a Bristol Gauge to record any observed leakage.
P32 | PAW | Pumped Acid Waste | Pumped Discharge acid waste piping Above Ground | Hot dipped galvanized seamless carbon steel pipe, domestic made with grooved ends with Victaulic style couplings or screwed ends. | ASTM A-53S, grade A or B | Schedule 40 | Screwed Mechanical or Victaulic style couplings | Galvanized Victaulic couplings are acceptable. "No-hub" type couplings are prohibited for this application. | Option 1: Rising stem full ported cast iron gate valve, class 300#, ASME B 16.4; ASME B16.12; ASTM A 74; ASTM A 888; CISPI 301. Option 2: Pipes 3"- 5": NIBCO LD3122-3. Pipes 6" and above: NIBCO LD3122-5 lug style butterfly valves. Raised full faced spiral wound gaskets and B16 studs and nuts. Isolation valves installed higher than 10' above finished floor shall have chain operated hand wheel. | N/A | N/A | N/A | Yellow / Black | Piping includes all discharge piping with earthquake strap from units to a point of connection where pump discharge connects to gravity drainage line. "No-hub" couplings are not acceptable on any pumped discharge line. | Minimum 3 inch wide polyethylene detectable type marking tape. The tape shall be resistant to alkalis, acids and other destructive agents found in soil and impregnated with metal so that it can be readily recognized after burial by standard locating equipment. 1. Lamination bond of one (1) layer of Minimum 0.35 mils thick aluminum foil between two (2) layers of minimum 4.3 mils thick inert plastic film. 2. Minimum tensile strength: 63 LBS per 3 In width. 3. Minimum elongation: 500 percent. | Pressure test piping system either hydrostatically with water as the testing medium or pnuematically with either compressed air or nitrogen as the testing medium. Pipes smaller than and equal to 2.5" diameter shall be tested using either the hydrostatic or pneumatic methods Pipes larger than 2.5" diameter shall be tested using a combination of hydrostatic and pnuematic testing using 95% water by volume and 5% compressed air to minimize any potential risks posed by stored energy in compressed air. Pipes shall be tested with a pressure of not less than 1.5 times the operating pressure but not less than 100 psig. Test pressure shall be held for a minimum period of 4 hours; use a Bristol Gauge to record any observed leakage. | N/A
P33 | NG | Natural Gas | Direct Buried, Below Grade, Downstream of the gas meter and within 5 feet outside of the building | Piping 2" and smaller: "Fletcher" coated seamless Schedule 40 carbon steel, ASTM A106 or ASTM A53 Type "S", Grade A or B. Piping 2.5" and larger: Type "S" seamless Schedule 40 black steel, ASTM A53, Grade A or B. (ERW, longitudinal seam and imported piping are not acceptable) | ASTM A-53S, grade A or B, US made, seamless | Schedule 40, Carbon steel, "Fletcher" coated | Butt or socket welded joints shall be made using factory-fabricated steel welding fittings. De-burr, clean, apply primer and wrap all joints that are not "Fletcher" coated. | Class 150 black malleable iron threaded fittings conforming to ASME B16.3. With Schedule 40 wrought carbon steel fittings, ASTM A 234 and butt welded joints. | Line Shut-off Valves sizes 2 inches and smaller: Iron body lubricated plug valve conforming to ASTM-A-126, U.L. Listed and A.G.A. Approved for natural gas service with threaded ends, wrench operation, rated for 200 WOG service pressure and –20 to 200 degrees F; manufactured by Resun "Model R-1430" or Nordstrom "Model 142C". Line Shut-off Valves sizes 2½ inches and larger: Iron body lubricated plug valve conforming to ASTM-A-126, U.L. Listed and A.G.A. Approved for natural gas service with flanged ends, wrench operation, rated for 200 WOG service pressure and –20 to 200 degrees F; manufactured by Resun "Model R-1431" or Nordstrom "Model 143". | N/A | N/A | N/A | Yellow / Black | When "Fletcher" coated pipe is not being installed, follow alternate materials and procedures: Surface preparation: De-burr and clean pipe. Wipe entire pipe surface and eliminate any grease & other chemicals and apply appropriate type of primer prior to coating or wrapping the pipe. Epoxy coat pipe at the factory or the job site or sleeve it with 150 mil Polyethylene with fused joints to achieve water impermeable joints. Additionally, Wrap the outside of the pipe with (2) half lapped layers of 20 mil PVC tape (40 mil min.) to make joints waterproof. ----- Alternate products: Field applied pipe coating shall be one of the following types: 1. Coal Tar Enamel Coating: Exterior of pipe and fittings shall be cleaned, primed with Type B primer and coated with hot-applied coal tar enamel with bonded layer of felt wrap in accordance with AWWA C203. Asbestos felt shall not be used; felt material shall be fibrous glass mat as specified in Appendix Section A2.1 of AWWA C203. 2. Adhesive-thermoplastic Resin Coating: Fed. Spec. L-C-530, Type I 3. Thermosetting Epoxy Coating: Fed. Spec. L-C-530, Type II 4. Field-applied PVC tape used on pipe joints and for repairing damaged areas of shop-applied coatings, Fed. Spec. L-T-1512, Type I, 10 mils nominal thickness for pipe joints, and Type II, 20 mils nominal thickness for coating repairs. |  | 1) Natural gas systems shall be inspected, tested, purged and placed into operation by a Licensed Plumber in accordance with NFPA 54. 2) Test under air pressure to 10 psi for 2 hours. Pressure tests shall be witnessed, recorded and countersigned by the Caltech Inspector. 3) After testing is complete, the entire gas system shall be purged with dry nitrogen to eliminate all air, debris and moisture from the piping before natural gas is introduced into the system. 4) After successful results of pressure test and purging have been completed, a leakage test shall be performed in accordance with NFPA 54 Appendix C. 5) Pressure test gas piping sleeve system with clean, dry compressed air at 15 pig by temporarily sealing all openings between gas carrier pipe, sleeves and vent openings. Sleeve systems must be demonstrated to be absolutely tight when subjected to this pressure for a period of four hours. | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements. Supports shall be designed for seismic zone 4.
P34 | NG | Natural Gas | Above Ground | Piping 2" and smaller: Seamless Schedule 40 carbon steel, ASTM A106 or ASTM A53 Type "S", Grade A or B. Piping 2.5" and larger: Type "S" seamless Schedule 40 black steel, ASTM A53, Grade A or B. (ERW, longitudinal seam and imported piping are unacceptable) | ASTM A-53S, grade A or B, US made, seamless | Schedule 40, Carbon steel | Threaded joints. Pipe joint compound shall be lead-free, non-toxic, non-hardening, insoluble in the presence of natural gas and compliant with ANSI/NSF 61 and Federal Specification TT-S-1732. Temperature service range of -15 degrees F to +400 degrees F, manufactured by "Hercules MegaLoc" or approved equal by Rectorseal, La-Co or Oatey. | Class 150 black malleable iron threaded fittings conforming to ASME B16.3. With Schedule 40 wrought carbon steel fittings, ASTM A 234 and butt welded joints. | Appliance/Equipment Shut-off Valves at local connections sizes 2 inches and smaller shall be bronze body, full port ball or butterfly type, U.L. Listed and A.G.A. Approved for natural gas service with threaded ends, quarter turn lever handle operation, rated for 175 W.O.G. service pressure and 30 to 275 degrees F., manufactured by NIBCO "Model T585-70-UL", "Model T580-70-UL" or Milwaukee "Model BB2-100". Manual Emergency Shut-off Valves sizes 2 inches and smaller shall be bronze body, full port ball or butterfly type, U.L. Listed and A.G.A. Approved for natural gas service with threaded ends, quarter turn lever handle operation, rated for 175 W.O.G. service pressure and 30 to 275 degrees F., manufactured by NIBCO "Model T585-70-UL", "Model T580-70-UL" or Milwaukee "Model BB2-100". | N/A | N/A | N/A | Yellow / Black | 1. All exposed piping 2" and smaller located within areas utilized as return air plenums shall have welded joints with Schedule 40 socket welded forged steel fittings conforming to ASME B16.11. 2. All exposed piping 2" and smaller serving laboratories from main natural gas riser to each shut-off valve shall have welded joints with Schedule 40 socket welded forged steel fittings conforming to ASME B16.11. |  |  | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements. Supports shall be designed for seismic zone 4.
P35 | RCW | Reclaimed Water for trap primers, irrigation water, urinals and water closets only | Inside The Building | Pipes up to 4": Seamless copper tubing (No ERW, longitudinal seam and imported piping are allowed.) | ASTM B88 | Type L, hard drawn, hot temper, entire exterior of pipe shall be painted or coated with purple color | 1) Braze with 15% silver content "Sil-Fos" brazing alloy. 2) Provide FxF threaded unions and FxF threaded isolation valves. 3) Exposed to view at plumbing fixtures and finished equipment, satin finish CP brass pipe with threaded cast bronze fittings. 4) No soft solder allowed except within 6" of threaded couplings. | 1) Wrought copper solder sweat type, ANSI B16.22 or brass castings, ANSI B16.18 2) Press fittings as manufactured by Viega "ProPress", Mueller "Streamline" PRS, or Elkhart "Apollo Press" | Pipes up to 2": NIBCO T-585-70-66-LF Pipes 2.5": NIBCO T-585-66 Pipes 3"- 5": NIBCO LD3122-3. Pipes 6" and above: NIBCO LD3122-5 lug style butterfly valves. Raised full faced spiral wound gaskets and B16 studs and nuts. All components associated with potable water system shall be lead-free (NSF-372/NSF-61G) | Rigid Fiberglass, ASTM C335, K = 0.24 at 75F, Owens Corning, Certainteed or John Manville | Pipe up to 1": 1" thick fiberglass. Pipe 1.25" & above: 1.5" thick fiberglass | Exposed Indoors: ASJ + 30mil PVC / Outdoors: ASJ + 0.016" Aluminum (0.032" Aluminum when subject to damage) | RCW: Purple / White. All reclaimed water pipe shall be wrapped with an 8 mil thick layer of polyethylene film, purple in color and conforming to ANSI/AWWA C105/A21.5 | Run mains at evenly pitched 1 inch in 50 feet. Make allowance for expansion in all piping installation so that the usual variation in temperature will not cause stress at any point. Securely anchor where necessary to distribute expansion stresses. Provide 1" drainage valve at low points. Anchor all lines and risers as necessary to prevent noise or vibration when water is turned on or off. Separately valve each branch and riser. Make all such valves accessible with approved type panels. Balance, vent and adjust piping to provide circulation to all fixtures and to prevent water hammer. | Pipe supported on firm sand bed for entire length. [CPC 314.3] No rocks supporting or touching pipes. [CPC 315.4] Six inches of sand bed minimum for ABS/PVC drain pipe per manufacturer, No rocks or debris in first 12” of backfill over ABS pipe. [CPC 315.4] Trenches not to undermine footings within bearing plane (45˚). [CPC 315.1] Sewer and water pipe to be buried minimum 18” deep. [CPC 609.1] | Same as above + install minimum 3 inch wide polyethylene detectable type marking tape over buried pipe. The tape shall be resistant to alkalis, acids and other destructive agents found in soil and impregnated with metal so that it can be readily recognized after burial by standard locating equipment. 1. Lamination bond of one (1) layer of Minimum 0.35 mils thick aluminum foil between two (2) layers of minimum 4.3 mils thick inert plastic film. 2. Minimum tensile strength: 63 LBS per 3 IN width. 3. Minimum elongation: 500 percent. 4. Provide continuous yellow with black letter printed message repeated every 16 to 36 inches warning of pipe buried below (e.g.: "CAUTION RECLAIMED WATER PIPE BURIED BELOW") | N/A
P36 | RCW | Reclaimed Water for trap primers, irrigation water, urinals and water closets only | Outside the building and direct buried | AWWA C900 PVC pipe, DR18 / 200 PSI pressure class | Material cell classification material cell 12454-8 per ASTM D 1784 | PVC, purple color | Provide polyvinyl chloride (PVC) couplings with twin elastomeric gaskets/ retaining glands which are designed to connect straight ends of plain pipe and allow 2 degrees of deflection at each gasket for a total of 4 degrees per coupling. | Ductile iron fittings or AWWA-C900 PVC | Pipes up to 2": NIBCO T-585-70-66-LF Pipes 2.5": NIBCO T-585-66 Pipes 3"- 5": NIBCO LD3122-3. Pipes 6" and above: NIBCO LD3122-5 lug style butterfly valves. Raised full faced spiral wound gaskets and B16 studs and nuts. All components associated with potable water system shall be lead-free (NSF-372/NSF-61G) | N/A | N/A | N/A | RCW: Purple / White. All reclaimed water pipe shall be wrapped with an 8 mil thick layer of polyethylene film, purple in color and conforming to ANSI/AWWA C105/A21.5 | Install concrete anchor thrust blocks or tie-rods on all underground lines at all tees and elbows to prevent movement when under pressure. All tie-rods, clamps, brackets, and bolts shall be ductile iron, stainless steel, galvanized or epoxy coated. Flanged restraints shall be similar to "MEGALUG series 1100" or "MEGALUG 1700 series". Sterilize the system by introducing chlorinating solution into the entire system for a minimum period of 24 hours. Maintain concentration of 50-150 ppm. Residual chlorine not to exceed 0.2 ppm. |  | Same as above + install minimum 3 inch wide polyethylene detectable type marking tape over buried pipe. The tape shall be resistant to alkalis, acids and other destructive agents found in soil and impregnated with metal so that it can be readily recognized after burial by standard locating equipment. 1. Lamination bond of one (1) layer of Minimum 0.35 mils thick aluminum foil between two (2) layers of minimum 4.3 mils thick inert plastic film. 2. Minimum tensile strength: 63 LBS per 3 IN width. 3. Minimum elongation: 500 percent. 4. Provide continuous yellow with black letter printed message repeated every 16 to 36 inches warning of pipe buried below (e.g.: "CAUTION RECLAIMED WATER PIPE BURIED BELOW") | N/A
P39
P37 | CW, FW, and RCW | Potable Cold Water, Fire protection water and reclaimed water | Inside utility tunnels and areaways | Hot dipped Galvanized Schedule 40 seamless carbon steel pipe with threaded, welded or cut grooved joints for sizes 2" and below. Mains may be flexible or rigid grooved couplings. Pipes 3" and over can be mechanical flexible grooved couplings. No Schedule 10 ASTM A-795 black steel pipe with roll-grooved or welded joints are allowed. | ASTM A-53S, grade A or B, seamless, Galvanized, Domestic made | Schedule 10 or Schedule 40, depending on the type of joint | Welded joints shall be made using factory-fabricated steel welding fittings. Grooved end malleable iron fittings and bolted clamp type malleable iron couplings with rubber sealing gaskets for grooved end pipe with appropriate pressure rating, similar to Victaulic "Style 75" may be used, except on dry pipe and/or pre-action systems, couplings shall be provided with rubber "flush seal" gaskets of the same manufacturer as the coupling and intended to be used together. | Standard weight carbon steel, butt weld ASTM B16.3. | listed fire protection valves, UL, ULC, FM global, and fire marshal listed and approved. See design guide for additional requirements. When used as a common FW+CW pipe, the isolation valves shall be lead-free. | N/A | N/A | N/A | Potable Cold Water-Green/White FW-Red/White RCW-Purple/White | All expansion joint fittings shall be FM approved. Provide ground joint type unions for 2 inch and smaller pipe, of galvanized iron with brass seats. Black and hot-dipped Zinc coated (Galvanized) welded and seamless steel pipe, ASTM A795: 1) Between Siamese and check valve, ball drip drains, drain and test piping subject to alternate wetting and drying, test and relief piping, water motor gong piping, and normal dry piping. 2) Fittings and couplings for galvanized shall be galvanized. Provide anti-microbial internal coating protection for all pipes. | Purge with nitrogen gas during brazing to prevent formation of oxides inside the pipe. No soft solder allowed except within 6" of threaded couplings. | Carbon steel, stainless steel and copper piping system shall be chemically cleaned for a minimum of 48 hours. Pressure test piping system either hydrostatically with water as the testing medium or pnuematically with either compressed air or nitrogen as the testing medium. Pipes smaller than and equal to 2.5" diameter shall be tested using either the hydrostatic or pneumatic methods Pipes larger than 2.5" diameter shall be tested using a combination of hydrostatic and pnuematic testing using 95% water by volume and 5% compressed air to minimize any potential risks posed by stored energy in compressed air. Pipes shall be tested with a pressure of not less than 1.5 times the operating pressure but not less than 100 psig. Test pressure shall be held for a minimum period of 24 hours. Record initial and final pressures. Repair any leaks, record the results with the name of the inspector and date of approval noted. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. Neutralize the chemicals and flush the system immediately after cleaning is completed and discharge the chemicals in accordance with the local codes and in compliance with CIT design guide. Refer to campus design guide document foot the details of cleaning & passivation procedures and chemicals. | N/A
P38 | HPA | High Pressure Compressed Air Main | Inside utility tunnels and areaways | Pipes 3" and smaller: Domestic Seamless copper, type L | ASTM B280 | ACR Type L, Hard drawn copper tubing | 1) Braze with 15% silver content "Sil-Fos" brazing alloy. 2) Provide FxF threaded unions and FxF threaded isolation valves. 3) Exposed to view at plumbing fixtures and finished equipment, satin finish CP brass pipe with threaded cast bronze fittings. 4) No soft solder allowed except within 6" of threaded couplings. | 1) Wrought copper solder sweat type, ANSI B16.22 or brass castings, ANSI B16.18 2) Press fittings as manufactured by Viega "ProPress", Mueller "Streamline" PRS, or Elkhart "Apollo Press" | Pipes up to 2": NIBCO T-585-70-66-LF. Pipes 2.5": NIBCO T-585-66 Pipes 3": NIBCO LD3122-3 lug style butterfly valves. Raised full faced spiral wound gaskets and B16 studs and nuts. | N/A | N/A | N/A | Yellow/Black | Compressed air piping shall be thoroughly cleaned and be free of any oxides, oils or particulates prior to being put into service. | Braze copper pipe joints and non-threaded fittings with 15% "Sil-Fos". Threaded fittings shall be soft-soldered using 95/5 lead -free solder. Care should be taken not to anneal the threads. Purge with Nitrogen gas during the brazing process to prevent formation of oxides. | Same as above | N/A
P39 | HPA | High Pressure Compressed Air Main | Inside utility tunnels and areaways | Pipes 4" and larger: Domestic (US made) Seamless Steel Pipe (No ERW, longitudinal seam and imported piping are allowed.) | ASTM A53-S, Grade A or B | Pipe 4" to 10": Schedule 40 Pipe 12" & above: Standard weight | Butt welded AWS D1.1 or flanged. For flanged fittings, use raised face flanges and metal wound gaskets. Mechanical joint couplings allowed at final connections to equipment to facilitate maintenance. | Standard weight carbon steel, butt weld ASTM B16.3. | Pipes 4"- 5": NIBCO LD3122-3. Pipes 6" and above: NIBCO LD3122-5 lug style butterfly valves. Raised full faced spiral wound gaskets and B16 studs and nuts | N/A | N/A | N/A | Yellow/Black | Compressed air piping shall be thoroughly cleaned and be free of any oxides, oils or particulates prior to being put into service. | Chemical cleaning, pickling and chemical passivation of stainless steel tubing and pipe is required. Follow procedures outlined in ASTM-A380 Standard Practice for Cleaning, De-scaling, and Passivation of Stainless Steel Parts, Equipment and Systems. | Same as above | N/A
P40 | DI | De-ionized Water main | Inside utility tunnels and areaways | Seamless stainless steel pipe, Grade 316L. ERW or longitudinal seamed pipes are unacceptable. | ASTM-A312 / ASME-SA312 | Schedule 10S | Gas Tungsten arc welding (GTAW) or Tungsten inert gas welding (TIG). Orbital welded, Butt welded or socket welded. | ASTM- A312/ASME-SA312 schedule 10 seamless stainless steel butt welded. | Full port ball valve, 2-piece body, blowout proof stem, 316 or 316L stainless trim & body construction, threaded ends, 1/4 turn lever handle. Conforms to MSS SP-110, as manufactured by NIBCO T-585-S6-R-66-LL. | N/A | N/A | N/A | Green / White | Deionized water piping shall be thoroughly cleaned and be free of any oxides, oils or particulate prior to being put to service. Materials shall be pre-cleaned. Scales shall be removed through chemical de-scaling, acid pickling, and mechanical de-scaling. Degreasing and general cleaning shall be accomplished by immersion in, swabbing with, or spraying with alkaline, emulsion, chelate, acid, solvent, or detergent cleaners or a combination of these; by vapor degreasing; by ultrasonics using various cleaners; by steam, with or without a cleaner; or by high-pressure water-jetting, as outlined in ASTM-A380. | Purge with nitrogen gas during brazing to prevent formation of oxides inside the pipe. No soft solder allowed except within 6" of threaded couplings. | Pressure test piping system either hydrostatically with water as the testing medium or pnuematically with either compressed air or nitrogen as the testing medium. Pipes smaller than and equal to 2.5" diameter shall be tested using either the hydrostatic or pneumatic methods Pipes larger than 2.5" diameter shall be tested using a combination of hydrostatic and pnuematic testing using 95% water by volume and 5% compressed air to minimize any potential risks posed by stored energy in compressed air. Pipes shall be tested with a pressure of not less than 1.5 times the operating pressure but not less than 100 psig. Test pressure shall be held for a minimum period of 24 hours. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements. Supports shall be designed for seismic zone 4.
P41 | N2, carbogen, CO2, Argon and other non-reactive lab gases | Non-high purity lab gases such as high pressure Nitrogen main, etc. | Inside utility tunnels, areaways and other approved locations | Seamless copper tubing | ASTM B819 | OXY-MED grade Type L, hard drawn | 1) Braze with 15% silver content "Sil-Fos" brazing alloy. 2) Provide FxF threaded unions and FxF threaded isolation valves. 3) No soft solder allowed except within 6" of threaded couplings. | 1) Wrought copper solder sweat type, ANSI B16.22 or brass castings, ANSI B16.18 2) Press fittings as manufactured by Viega "ProPress", Mueller "Streamline" PRS, or Elkhart "Apollo Press" | Pipe up to 2.5": NIBCO T685-66 or NIBCO T-585-66 ball valves. | N/A | N/A | N/A | Yellow / Black | Nitrogen piping shall be thoroughly cleaned and be free of any oxides, oils or particulates prior to being to service. | Copper tubing shall be pre-filled from the factory with Nitrogen gas and delivered to the project site in clean and free of any contaminants. Braze copper pipe joints and non-threaded fittings with 15% "Sil-Fos". Threaded fittings shall be soft-soldered using 95/5 lead -free solder. Care should be taken not to anneal the threads. Purge with Nitrogen gas during the brazing process to prevent formation of oxides. | Pressure test piping system with compressed nitrogen for a minimum of 24 hours at 1.5 times maximum working pressure or 150 PSI minimum. Pressure test shall be observed by a Caltech inspection representative and signed off in writing. | As per latest applicable CPC, NFPA, FM global and fire marshal's requirements. Supports shall be designed for seismic zone 4.
P42 | FS | Fire sprinkler | Inside the building | Schedule 40 seamless carbon steel pipe with threaded, welded or cut grooved joints for sizes 2" and below. Mains may be flexible or rigid grooved couplings. Pipe 3" and over can be mechanical flexible grooved couplings. No Schedule 10 ASTM A-795 black steel pipe with roll-grooved or welded joints are allowed. | ASTM A-53S, grade A or B, seamless, Domestic made | schedule 40 | Welded joints shall be made using factory-fabricated steel welding fittings. Grooved end malleable iron fittings and bolted clamp type malleable iron couplings with rubber sealing gaskets for grooved end pipe with appropriate pressure rating, similar to Victaulic "Style 75" may be used, except on dry pipe and/or pre-action systems, couplings shall be provided with rubber "flush seal" gaskets of the same manufacturer as the coupling and intended to be used together. | Standard weight carbon steel, butt weld ASTM B16.3. | listed fire protection valves, UL, ULC, FM global, and fire marshal listed and approved. See design guide for additional requirements. Isolation valves installed higher than 10' above finished floor shall have chain operated hand wheel. | N/A | N/A | N/A | Red / White | All expansion joint fittings shall be FM approved. Provide ground joint type unions for 2 inch and smaller pipe, of galvanized iron with brass seats. Black and hot-dipped Zinc coated (Galvanized) welded and seamless steel pipe, ASTM A795: 1) Between Siamese and check valve, ball drip drains, drain and test piping subject to alternate wetting and drying, test and relief piping, water motor gong piping, and normal dry piping. 2) Fittings and couplings for galvanized pipes shall be galvanized. 3) Provide anti-microbial internal coating protection for all pipes. | Clean and flush pipes after installation | Testing shall be in accordance with NFPA standards, upon completion prior to acceptance of the installation subject the system to a hydrostatic pressure test with no visible leakage. Remove and replace all defects due to materials or workmanship occurring during the test and retest after corrections have been made. All testing shall be approved by Caltech and FM Global representatives and City of Pasadena Fire Inspector. The contractor shall complete two sets of FM Global's contractors material and test certificate for above ground piping. One set is for Caltech permanent records, and one is for FM global.
1) As an alternative to Enfield's polypropylene ACID waste and ACID vent pipe, JOSAM' 316L stainless steel AW & AV pipe may be acceptable, only when called out on the OPR, plans and specifications and approved by Caltech's mechanical engineer in writing. 2) NIBCO ball valve T-585-70-66 is only acceptable for ICW & IHW and other non-potable applications as this is a not a lead-free valve. T-585-66-LF is a lead-free valve and shall be required on the potable water system (DCW + DHW).