## Sheet1
Laboratory exhaust hood type, application & requirements
Date : 09/17/2026
Revision: V5.5
Special attributes (*#3) | CAV Fume hood, Constant air volume (*#4) | VAV Fume hood Variable air volume, (*#4) | Radio isotope hood (CAV) | Perchloric acid fume hood (CAV) | fume hood for HF and other highly corrosive chemicals (CAV) | Hybrid Hoods Human protection + laminar | Wet Bench, (*#1) | Floor-mounted or vertical fume hood | Biosafety cabinet, class II, type A2 | Biosafety cabinet , Class II, type B2, Total exhaust | Biosafety cabinet (Baker hood) | Laminar flow or clean bench (zero exhaust) | Canopy hood | Chemical storage cabinet | Ventilated gas cabinet | Snorkel exhaust
Exhaust / recirculation (%) | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | (Varies) | 100/0 | 30/70 | 100/0 | 0/100 | 0/100 | 100/0 | 0/100 | 100/0 | 100/0
Required face velocity occupied /unoccupied (FPM) | 100/60 | 100/60 | 100/100 | 100/100 | 100/100 | 100/0 | 100/100 | 100/100 | 100/100 | 100/100 | N/A | N/A | As prescribed by CMC | N/A | 100/100 at the view window opening area or as per manufacturer's recommendation | As per manufacturer's recommendation. Provide blast gate for positive shut-off
Intended purpose to protect: | personnel & environment | personnel & environment | personnel & environment | personnel & environment | personnel & environment | Primary personnel & environment Secondary - material protection | personnel, environment and material | Personnel, environment & Accommodate oversized apparatus | personnel, environment and material | personnel, environment and material | personnel, environment and material | material & environment | personnel & environment | personnel & environment | personnel & environment | Localized capture to protect personnel & environment
Typically used for capturing: | chemical vapors | chemical vapors | Radio-isotope active chemicals | Perchloric acid and other chemical vapors | Acid Digestion, HF, Piranha and other highly corrosive chemicals | FH Mode - chemical vapors Laminary mode - particulates only | chemical vapors and particulates | Accommodate oversized and bulky apparatus | Biological matter | Biological matter | Biological matter | particulates only, shall not be used with chemicals vapors | vent non-toxic materials, heat, steam and odors from large or bulky apparatus that do not require a physical barrier such as ovens, steam baths and autoclaves | chemical vapors | chemical vapors | Non-toxic chemical vapors, odors, soldering fumes and particulates
ASHRAE 110 test & certification by a certified independent contractor for 100% of hoods | At the factory | At the factory and as installed at the site when lab is re-configured | At the factory and as installed at the site when lab is re-configured | At the factory and as installed at the site when lab is re-configured | At the factory and as installed at the site when lab is re-configured | FH function - At the factory and as installed at the site when lab is re-configured Laminar - not regulated, use specific | At the factory and as installed at the site when lab is re-configured | At the factory and as installed at the site when lab is re-configured | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
face velocity/flow rate test & certification by Caltech or TAB contractor | Cal OSHA, ANSI, NFPA & AIHA | ASHRAE 110-2016, Cal OSHA, ANSI, NFPA & AIHA | ASHRAE 110-2016, Cal OSHA, ANSI, NFPA & AIHA | ASHRAE 110-2016, Cal OSHA, ANSI, NFPA & AIHA | ASHRAE 110-2016, Cal OSHA, ANSI, NFPA & AIHA | ASHRAE 110-2016, Cal OSHA, ANSI, NFPA & AIHA | ASHRAE 110-2016, Cal OSHA, ANSI, NFPA & AIHA | ASHRAE 110-2016, Cal OSHA, ANSI, NFPA & AIHA | OSHA | OSHA | OSHA | N/A | CMC and Industrial ventilation guide | N/A | ??? | N/A
Special certification requirements | in-house annual certification by EH&S at minimum 18" sash height | in-house annual certification by EH&S at minimum 18" sash height | in-house annual certification by EH&S at minimum 18" sash height | in-house annual certification by EH&S at minimum 18" sash height | in-house annual certification by EH&S at minimum 18" sash height | in-house annual certification by EH&S at minimum 18" sash height Specialized sensor calibration for fume hood and laminar, if present | in-house annual certification by EH&S at minimum 18" sash height | in-house annual certification by EH&S at minimum 18" sash height | Annual inspection & cert. by external resources | Annual inspection & cert. by external resources | Annual inspection & cert. by external resources | N/A | N/A | N/A | N/A | N/A
Filter and other special features | N/A | Hood-mounted occupancy sensor | Bag in/Bag out | Automatic wash-down with deionized water | Automatic wash-down with deionized water and drainage trough | Booste Fan HEPA | HEPA + provisions for capturing & handling liquid waste | N/A | HEPA | HEPA | HEPA | HEPA | N/A | self-closing doors+ventilation opening high and low with flash arrestors | Provide blast gate for positive shut-off | Provide blast gate for positive shut-off
Pressure independent EA flow TAU or valve | Yes | YES | Yes | Yes | Yes | YES | YES | Yes | N/A (thimble connection) | Thimble or direct exhaust | N/A | N/A | not required but recommended | N/A | not required but recommended | N/A
Automatic sash closer | Not required | required | Not required | Not required | Not required | required | N/A | Not required | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Work surface construction material (*#2) | solid Epoxy resin or 316L stainless steel | solid Epoxy resin or 316L stainless steel | solid Epoxy resin or 316L stainless steel | fire-retardant Polypropylene or PVC | fire-retardant Polypropylene or PVC | solid Epoxy resin or 316L stainless steel | perforated fire-retardant Polypropylene or PVC | N/A | solid Epoxy resin or 316L stainless steel | solid Epoxy resin or 316L stainless steel | solid Epoxy resin or 316L stainless steel | Varies | N/A | N/A | N/A | N/A
Electronic Low-flow alarm panel | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | N/R | N/R | N/A | N/A | N/A | N/A | N/A
Visual flow indicator, magnehelic , minihelic gauge | Yes, indicates exhaust duct pressure differential | Yes, indicates exhaust duct pressure differential | Yes, indicates exhaust duct pressure differential | Yes, indicates exhaust duct pressure differential | Yes, indicates exhaust duct pressure differential | Yes, indicates exhaust duct pressure differential * Hybrid hood might have speciliazed AFM for both FH and laminar flow. | Yes, indicates exhaust duct pressure differential | Yes, indicates exhaust duct pressure differential | indicate HEPA filter loading status | indicate HEPA filter loading status | indicate HEPA filter loading status | N/A | N/R but recommended to indicate exhaust duct pressure differential | N/A | N/A | N/A
flow capture characteristic | in-rush through the face | in-rush through the face | in-rush through the face | in-rush through the face | in-rush through the face | in-rush through the face | in-rush through the face & down-rush | in-rush through the face | in-rush through the face | in-rush through the face | in-rush through the face | N/A | in-rush through the face | N/A | in-rush through the face | in-rush through the face
Base cabinet | Acid, flammable or vacuum pump | Acid, flammable or vacuum pump | Acid, flammable or vacuum pump | Acid, flammable or vacuum pump | Acid, flammable or vacuum pump | Acid, flammable or vacuum pump | varies | none | none | none | none | none | none | none | none | none
Base cabinet ventilation | required | required | required | required | required | required | required | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Sash type | Vertical, horizontal or combination sashes as required or defined during the OPR process | Vertical, horizontal or combination sashes as required or defined during the OPR process | Vertical, horizontal or combination sashes as required or defined during the OPR process | Vertical, horizontal or combination sashes as required or defined during the OPR process | Vertical, horizontal or combination sashes as required or defined during the OPR process | Vertical, horizontal or combination sashes as required or defined during the OPR process | Vertical, horizontal or combination sashes as required or defined during the OPR process | Vertical, horizontal or combination sashes as required or defined during the OPR process | Vertical | Vertical | Vertical | none | none | none | none | none
Polycarbonate Safety shield | As per user's requirements | As per user's requirements | As per user's requirements | As per user's requirements | Required | As per user's requirements | As per user's requirements | Not required | Not required | Not required | Not required | Not required | Not required | Not required | Not required | Not required
Exhaust air duct | 316L Stainless steel | 316L Stainless steel | 316L Stainless steel | 316L Stainless steel | 316L Stainless steel | 316L Stainless steel | 316L Stainless steel | 316L Stainless steel | Galvanized steel | Galvanized steel | N/A | N/A | Galvanized steel or 316L stainless steel, welded seams and water-tight for steam exhaust applications | Galvanized steel | Galvanized steel | Galvanized steel
Terminal unit controller's communications protocol | open source, non-proprietary | open source, non-proprietary | open source, non-proprietary | open source, non-proprietary | open source, non-proprietary | open source, non-proprietary | open source, non-proprietary | open source, non-proprietary | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
*#1 ) Wet benches are typically used for semi-conductor applications Many features of wet benches are determined during OPR and lab programming phase. The mentioned features are typical and not necessarily applicable to every project.
*#2) work surfaces will vary according to specific type of research and chemical used. Some of the options are: wood, PVC, polypropylene, Trespa, solid epoxy, 316L stainless steel, etc. Exact material to be determined during OPR and lab programming phase.
*#3) Special attributes outlined here are typical and may vary according to the user group's needs/requirements. As such, the exact details will need to be developed during OPR and lab programming phase.
*#4) All fume hoods, HF, radio-isotope, perchloric acid and vertical hoods shall be designed as high performance hoods and capable of proper capture and certification at 60 FPM face velocity. (hoods are not allowed to operate at 100 fpm face velocity in California)
Note on O5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Do we mean flammables cabinet? If so, not ventilated
Note on P7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Fire Code requires 150 fpm
Note on B10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should be same as other hood types
Note on B11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Add ASHRAE 110
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All hoods are certified by external resources now (currently TSS)
Note on O13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See above...not ventilated
Note on A18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Does not need to be a mag, but mag does meet requirements
Note on A29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Delete. This does not make sense….