## 2026_ARCH
SUMMARY OF PROPOSED ADDS / CHANGES - ARCH | [6 empty] | Note: This change summary is provided for reference and highlights major revisions to the Design Guidelines. It is not intended to identify every change or requirement. The Project Team shall review the current Design Guidelines in their entirety and shall not rely solely on this summary.
ITEM # | DG SECTION # | TOPICS | CONTENT IN V5.4 | PROPOSED CONTENT | UPDATE STATUS | Comments
Column1 | Column2 | Column3 | Column4 | Column5 | Column7 | Column8
1 | Definitions | Caltech Historic Zone |  | Replaced with updated map | Incorporated
2 | General Requirements | Caltech Finance, Facilities, and Infrastructure Committee Project Approvals | Caltech Building and Grounds Committee Project Approvals | Approvals and reviews needed by the Finance, Facilities, and Infrastructure (FFI) committee of the Board of Trustees shall be coordinated with the Executive Director of Planning, Design & Construction. Approvals typically include capital construction projects with total project costs greater than $10 million, construction of new buildings, renovation of existing facilities, and projects intended to change exterior campus elements, including building exteriors and open space. | Incorporated
3 | General Requirements | Sustainability | In addition to being LEED certified and aligning with campus sustainability initiatives, Caltech would like the design team or the design builder to take advantage of the maximum reasonably achieved available incentives offered by local utilities. For instance, Pasadena Water & Power sponsors a High-Performance Building Program to encourage low-energy design by offering monetary incentives to owners who invest in a design that is lower than the required California Energy Code performance by at least 10%. The incentive is equal to the amount of electric bill savings for one year. | Removed | Incorporated
4 | General Requirements | Room Noise Criterion |  | Computer/server rooms 50–65 Lab equipment corridor 45–60 Corridors and public circulation areas 45–55 Open-plan offices 35–40 Private offices 30–35 Seminar Room 30–35 Conference Rooms 30–35 Classroom 30 Teaching Lab 30-35 Research Lab 35-45 Precision research Lab 25–35 | Incorporated
5 | General Requirements | Drone Use Application | Application form can be found and downloaded at http://forms.caltech.edu/Parking-Security/UAS_Application.pdf. Completed application form to be sent to Caltech PM for review and process. | Updated Link: Complete an Application for Use of Unmanned Aircraft Systems (Drones) & Other Airborne Objects form and send to Caltech PM for review and process. | Incorporated
6 | Project Delivery | Reference Drawings |  | No as buillt will be provided by Caltech, reference drawing is avaliable upon request. | Incorporated | various locations
7 | Project Delivery | Project Information - Permit Set |  | Permit application drawing shall include the Caltech building number, building name, floor(s) affected, and room number(s) affected by the project. The drawings shall also identify the Caltech PM, including contact email, and permit center's contact info. | Incorporated
8 | Project Delivery | Project Delivery Platform |  | Caltech will utilize Autodesk Construction Cloud (ACC) /Autodesk Forma as the project management platform. All project consultants and contractors should use ACC for project information management and coordination throughout planning, design, and construction. All project participants shall comply with Caltech ACC requirements. | Incorporated
9 | Project Delivery | Finish/Material Board |  | Provide a labeled finish/material board and schedule. Physical boards are preferred. Digital board may be acceptable for small projects with Caltech PM approval. Update finish/material boards and schedules throughout the design and construction phase to reflect approved selections and project changes. | Incorporated
10 | 01 56 00 | Temporary Tree and Plant Protection | Do not dump excess concrete, chemicals, or other liquid wastes within 10 feet of drip line of trees. | Do not dump excess concrete, chemicals, or other liquid waste on campus grounds, landscaped areas, or into storm drains. | Incorporated
11 | 01 56 00 | Temporary Site Management and Housekeeping |  | Provide and maintain adequate refuse containers for construction debris. Disposal of construction materials, packaging, and waste in Caltech trash or recycling receptacles is prohibited. Provide contractor restroom facilities for the duration of construction. Building restrooms and sinks shall not be used by construction personnel for routine use or for cleaning tools, equipment, or materials. Maintain construction, staging, and parking areas in a clean condition. Do not litter or leave debris on the ground. Do not park vehicles, equipment, or material storage on landscaped areas. Repair or replace in kind any items damaged by construction activities. Remove temporary utility location markings from concrete, paving, and other exposed surfaces at project closeout. Restore surfaces to original condition if markings cannot be completely removed. Temporary floor protection shall be installed in a manner that does not damage existing finishes. Upon removal, all tape, adhesive, and residue shall be completely removed from floor surfaces. | Incorporated
12 | 01 80 00 | Sustainable Design Requirement Renewable Energy |  | Caltech encourages the incorporation of renewable energy generation and energy storage systems in new construction and major renovations where technically and financially feasible. Project teams shall evaluate opportunities for on-site renewable energy integration and coordinate with Caltech Facilities and Sustainability during design. | Incorporated
13 | 02 41 19 | Office and Lab Cleanout Protocol |  | Prior to demolition activities, coordinate a site walk with the Caltech Project Manager, Recycling & Materials Coordinator, Recycling Lead, and Transportation Supervisor to identify materials and equipment designated for reuse, salvage, recycling, storage, resale, or disposal. Materials designated for salvage or resale will be removed by Caltech Transportation as part of project cost. Contractor to remove remaining demolition waste and provide waste diversion documentation at project closeout. | Incorporated
14 | 02 80 00 | Abatement |  | Provide third party oversight for abestos/lead abatement work. | Incorporated
15 | 07 50 00 | Roofing |  | Performance requirement for: a.Roof Penetration b.QA/QC Requirements c.Hazardous Material Testing d.Weather Protection/Temporary Waterproofing e. Project- Specific Requirements | Incorporated
16 | 08 00 00 | Exterior Openings |  | Any deviation or modification impacting exterior appearance, facade systems, windows, doors, glazing, or building envelope systems shall require review and approval by Caltech Facilities Planning, Engineering & Architecture and the Director prior to implementation. | Incorporated
17 | 08 71 00 | Keying Requirement - Cylinder |  | Manufacturer: Medeco, Schlage Primus for new construction Installation: For new construction, Caltech Lock Shop will supply and install permanent cylinders as part of the project cost. Contractor shall coordinate this work with CIT PM. Contractor is responsible for providing temporary construction cores. For renovation projects, Caltech Lock Shop will provide construction cores as part of the project cost. Contractor shall coordinate with CIT PM. | Incorporated
18 | 09 30 00 | Restroom/ Tiling Space Drainage |  | Floor surfaces in wet areas shall be sloped to the floor drain at a minimum of ¼ inch per foot (2%) to provide positive drainage and prevent standing water. | Incorporated
19 | 09 65 00 | Flooring Submittals |  | Provide full-size sample of each flooring type. Submit a minimum of two full units of each color, pattern, and type for review and approval. | Incorporated
20 | 09 65 00 | Lab VCT Flooring |  | Coordinate with Caltech PM and Buildings & Grounds regarding application of floor sealer and finish for VCT flooring in accordance with flooring manufacturer's recommendations. Protect newly installed resilient flooring from damage, staining, moisture, and construction traffic in accordance with the flooring manufacturer’s recommendations. Maintain protection until owner occupancy. At project closeout, flooring shall be clean and free of defects. | Incorporated
21 | 09 68 13 | Flooring Submittals |  | Provide full-size sample of each flooring type. Submit a minimum of two full units of each color, pattern, and type for review and approval. | Incorporated
22 | 09 69 00 | Flooring Submittals |  | Provide full-size sample of each flooring type. Submit a minimum of two full units of each color, pattern, and type for review and approval. | Incorporated
23 | 09 90 00 | Interior Paint |  | Interior Wall White Color Standard: Dunn Edwards or Sherwin Williams Caltech Pure White SW 7005, eggshell finish. Interior Ceiling White Color Standard: Dunn Edwards or Sherwin Williams Caltech Pure White SW 7005, flat finish. | Incorporated
24 | 09 90 00 | Concrete Flooring |  | Sealed Concrete: Provide clear sealer for exposed interior concrete floors where indicated. Coordinate sealer type, application method and maintenance requirements with Caltech PM and Buildings & Grounds prior to application. Polished Concrete: Provide mechanically polished concrete with protective sealer. Coordinate gloss level, finish, and maintenance requirements with Caltech PM and Buildings & Grounds prior to application. Provide field mock-up for Caltech's approval prior to full application. | Incorporated
25 | 10 11 00 | Markerboard installation height |  | Mount writeable surfaces so the centerline of the writing surface measures 60 inches AFF, unless otherwise required for the intended use, adjacent conditions or as indicated by PD&C. Coordinate mounting height with adjacent features including furniture, casework, receptacle locations as well as accessibility requirements. | Incorporated
26 | 10 14 00 | No Smoking Signs | Smoking is not permitted within 20 feet of a campus building | Smoking is not permitted within 25 feet of a campus building | Incorporated
27 | 10 14 00 | Eyewash, Safety shower, and Combination Sign |  | Eyewash, safety shower, and combination sign should project out from the wall and be visible throughout the room and include standard graphic design elements (pictograph) identifying the emergency equipment. The sign itself should be a blade-type sign. The background color should be green and the pictograph and any lettering should be white. The sign should be installed with an approved wall bracket centered directly above the emergency equipment’s location, at a height of 88" AFF (to the bottom of the sign) if ceiling height and other conditions permit. Any exceptions regarding placement should be approved by the Caltech Project Manager. | Incorporated
28 | 10 14 00 | Room Numbering | Rooms along a corridor shall be numbered with even numbers on one side and odd numbers on the other in a systematic fashion to mirror the Pasadena Street grid system where possible. Individual room numbers must be approved by Caltech. | Rooms along a corridor shall be numbered with even numbers on east and south sides and odd numbers on west and north sides, to mirror the Pasadena street grid system. Individual room numbers must be approved by Caltech. | Incorporated
29 | 10 21 00 | Anti-graffiti Coating |  | For renovation projects where existing toilet compartments are retained that do not provide graffiti-resistant surfaces, provide a manufacturer-approved anti-graffiti coating or protective covering. Coordinate with Caltech PM and ensure the treatment does not void existing warranties. | Incorporated
30 | 10 26 00 | Corner Guards |  | 6 feet default height, discuss with Caltech Planning, Design & Construction for special consideration/recommendation. | Incorporated
31 | 10 28 13 | Warm-Air Dryer | Warm-Air Dryers: 1) Recommend: Designed to have a sound pressure level of 69dB(A) | Removed | Incorporated
32 | 10 28 13 | Sanitary Dispensers | Sanitary Dispensers: Each Women’s restroom shall have a sanitary napkin and tampon dispenser unit with a "Free" operation dispenser(note: We no longer fill 25 cent dispensers-items are to be provided free and dispensed from baskets in restrooms). | Provide “free/no-cost” sanitary napkin and tampon dispensers in women’s and all-gender restrooms. | Incorporated
33 | 10 28 13 | Soap Dispensers | Recommend: Bobrick B-828 | LumeCell dispenser (Rubbermaid Commercial Products), black or chrome finish. | Incorporated
34 | 10 28 13 | Fume Hood Location |  | EH&S and the designated design professional shall jointly review hood locations during design to minimize cross drafts and traffic impacts.” | Incorporated
35 | 11 53 13 | ADA Fume Hoods |  | Where ADA accessibility is required, consider side-approach fume hood configurations. Coordinate accessibility requirements with the project design professional and Caltech PM. | Incorporated
36 | 11 53 13 | Fume Hood Manufactuers | Fisher Hamilton L.L.C. Kewaunee Scientific Corporation; Laboratory Products Group. Labconco Corporation. Jamestown Metal products (JMP) Hanson Lab Furniture Inc. Substitutions as allowed in writing by CIT Project Manager. | Hamilton Laboratory Solutions Kewaunee Scientific Corporation; Laboratory Products Group Labconco Corporation Mott Manufacturing Hanson Lab Solutions Inc. Labconco Earlab Substitutions as allowed in writing by Caltech project manager. | Incorporated
37 | 11 53 13.30 | Biosafety Cabinet Location |  | BSCs shall be located away from activities or facilities that produce air currents or turbulence. Locate away from high traffic areas, air supply diffusers, doors, and operable windows. BSCs should not be located adjacent to a single means of access to an exit. Recommendation is that BSCs be located more than 6 feet from any door or doorway and another directly facing BSC. | Incorporated
38 | 12 32 00 | Restroom Casework |  | Countertops: Provide solid surface material countertops. Plastic laminate countertops are not permitted. Fabricate tops in one piece, as much as possible. Comply with solid surfacing material manufacturer’s written recommendations for adhesives, sealers, fabrication, and finishing. Cabinet/Casework: Particle board–based surfaces are not permitted in wet areas. | Incorporated
39 | 12 35 53 | Epoxy Resin Sink | Epoxy Resin Sink: No drop-in sink allowed. Sinks in lab space to be integral or under mounted. Sealant: Join work surface and sinks with a two-part epoxy cement (Smooth—on) or a lab grade silicone as required | Epoxy Resin Sink: No drop-in sink allowed. Sinks in lab space to be under mounted. Sealant: Join work surface and sinks with a lab grade silicone as required. | Incorporated
40 | 12 35 53 | Lab Casework |  | Lab casework shall comply with SEFA 8 requirements. General requirement updates throughout, primarily for wood casework. Refer to the section for updates. | Incorporated
41 | 12 35 53.13 | Metal Lab Casework |  | Metal lab casework shall comply with SEFA 8M in addition to SEFA 8 requirements. Refer to the section for updates. | Incorporated
42 | 12 91 00 | Interior Waste and Recycling Receptacles |  | General: Substitutions and placement locations of the following items require approval from Caltech Planning, Design & Construction and FOS Building and Grounds. 1. Laboratory and Common Area Recycling Containers: Provide 23–gallon blue recycling containers by Rubbermaid Commercial Products (Slim Jim series) or Continental Commercial Products. Units shall be suitable for commercial institutional use. 2. Recycling Lids: Provide compatible 23–gallon recycling lids for containers, color-coded for waste stream identification in accordance with campus standards. 3. Office Recycling Wastebaskets: Provide 7–gallon blue recycling wastebaskets by Rubbermaid Commercial Products for office areas. Units shall be suitable for commercial institutional use. | Incorporated
43 | 14 20 00 | Anti-graffiti Coating |  | Recommend application of a clear graffiti-resistant protective coating (Graffiti Shield or approved equal) on exposed interior wall panels. | Incorporated
44 | 32 33 00 | Exterior Waste and Recycling Receptacles/Trash Bin |  | Coordinate location and each type of waste and recycling receptacles/trash bin with Caltech. | Incorporated
45 | 32 33 00 | Cigarette Urns | Doty & Sons Concrete Products; Model D; 18–inch diameter by 29 inches high, with sign stating, “PLEASE DEPOSIT CIGARETTES HERE.” Provide at least one cigarette urn. | Removed | Incorporated
46 | 32 80 00 | Irrigation |  | General: Caltech is in the process of updating the Central Irrigation Control System to the Calsense CS3000 a cloud based, advanced, smart irrigation management system. New Irrigation: - Controller shall be the Calsense CS3000 (or newer) including the cellular kit with a master control valve and flow sensor. This installation must be verified by a Calsense representative to ensure warranty. - Drip irrigation must be approved by CIT Grounds. No Drip system on lawns. - Quick coupler devices every 50 feet. - Installation of ball valve before every remote-control valve for emergencies. - SCH80 pipe used before and after remote control valves, ball valves, gate valves, etc. Materials: - Controller: Rain Bird ESP–40–SAT–TW–WM (12, 24, 32 station capability) Calsense CS3000 or newer - Remote control valves: Rain Bird (PEB/PGA) - Nozzles: Rain Bird 1800 series - Primer: Weld-On P-70 primer - Glue: Christy’s Red Hot Blue Glue, Christy’s Gray PVC Pipe cement (SCH80, PVC>1.5”) - Rotary nozzles: Rain Bird R-Van or Hunter MP Rotator Construction Requirements: a. Install temporary water submeters to monitor construction water usage. Submit water usage records and summary reports to Caltech PM at project closeout. b. Document existing irrigation systems and landscape conditions with photographs prior to construction. Restore or replace any damaged irrigation components, planting, or landscape improvements in kind. | Incorporated
47 | 32 90 00 | Landscaping |  | After final completion, routine mowing and watering may be performed by Caltech. However, the contractor shall remain responsible for all warranty requirements. | Incorporated
48 | APPENDIX V | Construction Issue Log |  | Replaced AiM with Autodesk Forma (ACC) | Incorporated
49 | APPENDIX IX | New Professorial Hires Office Renovation | Paint ceiling, or replace damaged ceiling tiles. Do not paint ceiling tiles. | Paint ceiling grid, or replace damaged ceiling tiles. Do not paint ceiling tiles. | Incorporated
50 | APPENDIX IX | New Professorial Hires Office Renovation | Office furniture may include sit-stand desks, modular casework, desk chairs, credenza, couches, side or guest chairs, and conference tables located inside the office. Should furniture needs exceed the allowed $20,000 renovation office budget, use of the divisional decentralized reserve is acceptable. | Office furniture may include sit-stand desks, modular casework, credenza, couches, side or guest chairs, and conference tables located inside the office. Should furniture needs exceed the allowed $20,000 renovation office budget, use of the divisional decentralized reserve is acceptable. | Incorporated
51 | APPENDIX IX | New Professorial Hires Office Renovation | Minimal electrical work, if not already existing: Two network outlets and one phone outlet | Minimal electrical work, if not already existing: Two network outlets | Incorporated
52 | APPENDIX IX | New Professorial Hires Office Renovation | For IT, Monitor bracket or projector mount only. HDMI conduit and cabling is provided for HDMI and outlets to support equipment where missing. Changes should not result in phone and/or data jacks becoming inaccessible (behind furniture or covered by wall treatments). If data ports are relocated, existing cabling is not to be pulled back to the telecommunications closet and reused. New cat 6A cable to be pulled. | For IT, Monitor bracket or projector mount only. Changes should not result in phone and/or data jacks becoming inaccessible (behind furniture or covered by wall treatments). If data ports are relocated, existing cabling is not to be pulled back to the telecommunications closet and reused. New cat 6A cable (coordinate with IMSS) to be pulled. " | Incorporated
53 | APPENDIX IX | New Professorial Hires Office Renovation | Division provided items—such as monitors, projectors, projector screens, artwork, cameras, speaker systems, ancillary equipment, refrigerators, coffee stations, etc.—are not included. | Division provided items—such as monitors, projectors, projector screens, artwork, cameras, speaker systems, ancillary equipment, refrigerators, coffee stations, task chair, etc.—are not included. | Incorporated
54 | APPENDIX XVIII | New Professorial Hires Office Renovation | General Construction Safety Guide | General Contractor Safety Guide | Incorporated
55 | APPENDIX XXII - OLAR Requirements | Floor | The floor will consist of material that will withstand constant contact with caustic sterilant (i.e. Clidox) and can withstand point pressure on casters for racks that may exceed 500lbs. Radial cove to join with wall. Radial coves shall have backing to support surface materials. Cove radius to be approved by OLAR personnel. | The floor will consist of material that will withstand constant contact with caustic sterilant (i.e. Clidox and accelerated hydrogen peroxide) and can withstand point pressure on casters for racks that may exceed 500lbs. Radial cove (6 inches) to join with wall should be seamless to drywall to prevent accumulation of debris at wall transition. Radial coves shall have backing to support surface materials. | Incorporated
56 | APPENDIX XXII - OLAR Requirements | Floor | Floor material type and color to be approved by OLAR personnel. | Floor material type and color to be approved by OLAR personnel. Epoxy or urethane based system are preferred. | Incorporated
57 | APPENDIX XXII - OLAR Requirements | Wall | Sani-rail and stainless steel corner guards will be installed in high traffic areas (e.g. hallways, food and bedding room, storage room) to protect wall finishes. | Sani-rail and stainless steel corner guards will be installed in high traffic areas (e.g. hallways, food and bedding room, storage room) and in areas with large equipment (e.g. cagewash, non-human primate housing spaces) to protect wall finishes. Plastic wall guard material will be placed in animal holding rooms at the level of contact with biosafety cabinets and animal housing racks. | Incorporated
58 | APPENDIX XXII - OLAR Requirements | Ceiling | Ceiling access panels with be 24” x 24” dimension (minimum), stainless steel, and gasketed to prevent entry of vermin (clean room seal). They will be located outside of the animal housing rooms. | Ceiling access panels will be minimum 24” x 24, stainless steel, and gasketed to prevent entry of vermin (clean room seal). They will be located outside of the animal housing rooms. Ceiling entry from an interstitial space above the facility is preferred in lieu of ceiling access in the animal facility corridors. Animal facilities should have hard lid ceilings. Exposed duct work is to be avoided. | Incorporated

## 2026_MECH-PLUMB
SUMMARY OF PROPOSED ADDS / CHANGES - MECH-PLUMB | [6 empty] | Note: This change summary is provided for reference and highlights major revisions to the Design Guidelines. It is not intended to identify every change or requirement. The Project Team shall review the current Design Guidelines in their entirety and shall not rely solely on this summary.
ITEM # | DG SECTION # | TOPICS | CONTENT IN V5.4 | PROPOSED CONTENT | UPDATE STATUS | Comments
Column1 | Column2 | Column3 | Column4 | Column5 | Column7 | Column8
1 | Plumbing Fixtures and Products Table | Plumbing Fixtures | Make: Elkay | Make Elkay or Oasis | Incorporated
2 | Plumbing Piping | High Pressure Air and Vacuum | 3) Press fittings as manufactured by Viega Proppress, Mueller Streamline PRS, or Elkhart Apollo Press | 3) Press fittings are acceptable only with Caltech's permission. | Incorporated.
3 | 23 31 00 HVAC Ducts and Casings | Opening protection |  | At the time of rough installation and during storage on the construction site until final startup of the heating, cooling, and ventilating equipment, all duct and other related air distribution component openings shall be covered with tape, plastic, sheet metal, or other methods acceptable to the enforcing agency to reduce the amount of dust, water, and debris that may enter the system. Once installed, the duct section shall be wiped clean and a plastic taped cap installed on the open end of ductwork at any point when the duct is not being actively worked on. During construction activities generating dust within areas containing installed ductwork or air distribution components, the contractor shall implement dust control measures, including the use of negative air machines equipped with HEPA filtration where required to maintain construction area under negative pressures and minimize migration of dust into duct systems. If at any time the Caltech representative sees that this procedure is not being used, the contractor shall provide, at no cost to Caltech, a high-pressure vacuum cleaning of the ductwork prior to the TAB contractor’s work. | Incorporated.
4 | 22 05 53 Identification for Plumbing Piping and Equipment & 23 05 53 Identification for HVAC Piping and Equipment | Pipe Identification |  | Manufacturer: "Brady" or "Seton Setmark" Pipes < 6" outside diameter: Pre-coiled type snap-around labels. Pipes > 6" outside diameter: Flat type snap-around labels with metal ties. | Incorporated.
5 | 23 05 93 Testing, Adjusting, and Balancing (TAB) for HVAC | TAB reporting |  | Post TAB QA/QC spot checks shall be performed for critical areas including laboratories, cleanrooms, vivaria, and other pressure-sensitive spaces. The extent of the spot checks shall not exceed 50% of the TAB scope for critical areas. | Incorporated.
6 | 23 05 93 Testing, Adjusting, and Balancing (TAB) for HVAC | TAB reporting |  | Post TAB QA/QC spot checks shall be performed for non-critical areas including offices, corridors, and support spaces. The extent of the spot checks shall be 20% of the TAB scope for non-critical areas. | Incorporated.
7 | 23 05 93 Testing, Adjusting, and Balancing (TAB) for HVAC | TAB reporting |  | TAB tolerances indicated in this section are target values. Air quantities within +/– 3% of design values shall be acceptable, provided required system operation and pressure relationships are maintained. Caltech may require +/– 1% tolerance of designated critical spaces. | Incorporated.
8 | 23 05 93 Testing, Adjusting, and Balancing (TAB) for HVAC | TAB reporting |  | Caltech will randomly spot check approximately 10% of the TAB scope to verify TAB results. The TAB contractor and mechanical subcontractor shall cooperate with these verification activities and provide access to contractor provided equipment, systems, and TAB documentation as required. Bidders shall account for this requirement in their bid. Testing equipment and activities will not be provided or performed by Caltech. | Incorporated.
9 | APPENDIX XX - Standard Details | DTL 1 |  | Revised Detail | Incorporated.
10 | APPENDIX XX - Standard Details | DTL 2 |  | Revised Detail | Incorporated.
11 | APPENDIX XX - Standard Details | DTL 3 |  | Revised Detail | Incorporated.
12 | APPENDIX XX - Standard Details | DTL 20 |  | Revised Detail | Incorporated.
13 | APPENDIX XX - Standard Details | DTL 22 |  | Revised Detail | Incorporated.
14 | APPENDIX XX - Standard Details | DTL 25 |  | Revised Detail | Incorporated.
15 | APPENDIX XX - Standard Details | DTL 44 |  | Revised Detail | Incorporated.
16 | 23 73 00 Indoor Central-Station Air-Handling Units - Custo-Packaed, Outdoor, Central-Station Air-Handling Units | Features and Construction |  | Motor removal rail and trolley system shall be required for all motor assemblies weighing more than 50 lbs. Rail and trolley system shall be factory designed and installed in the air handler fan cabinet by unit manufacturer. Rail and trolley system shall be positioned directly over the motor and perpendicular to the side of the air handler. Provide with additional extendable rail to hoist motor outside the air handler | Incorporated.
17 | 23 05 23 General-Duty Valves for HVAC Piping | Valves | Nibco or Apollo | Nibco | Incorporated.
18 | 23 31 00 HVAC Air Distribution | Ductwork HVAC Air Distribution |  | Outdoor horizontal ducts shall be pitched and provided with drainage outlets to prevent pooling water on top. | Incorporated.
19 | 22 40 00 Plumbing Fixtures | Emergency Fixtures |  | Emergency eyewash and emergency showers shall be field tested prior to occupancy. | Incorporated.
20 | 23 00 00 - HVAC Systems | HVAC condensate |  | Condensate waste pipes from HVAC cooling coils shall be sized in accordance with the equipment capacity as follows: 1) Minimum condensate waste pipe size shall be sized per the California Mechanical Code and California Plumbing Code, but not less than 1–inch in size and not smaller than the equipment outlet size. 2) Pipe slope, point of discharge / disposal, and material selection shall minimally comply with the California Mechanical Code, California Plumbing Code, engineering drawings, and specifications. | Incorporated.
21 | 23 00 00 - HVAC Systems | Air Handling Unit Manufacturers | Thermal, Alliance, Scott-Springfield, Energy Labs, Temtrol | Thermal, Alliance, Dynamic Air Technology, Energy Labs | Incorporated.
22 | 23 00 00 - HVAC Systems | Smoke Fire Damper Manufacturers | Ruskin, Greenheck, United Enertech | Rusking, Greenheck, Unitied Enertech, Porrorff | Incorporated.
23 | 21 05 00 - Common Work Results for Fire Suppression | Pipe Sleeves |  | Fire sprinkler riser penetrations through the floor slab shall be sleeved 4 inches above finished floor and sealed water-tight to prevent potential flooding of the level below. Daylights or gaps through the floor slab without sleeves are not acceptable. Refer to section 23 00 00 for additional sleeve requirements. | Incorporated.
24 | Section 22 00 00 - Plumbing Systems | Pipe Sleeves |  | Plumbing riser penetrations through the floor slab shall be sleeved 4 inches above finished floor and sealed water-tight to prevent potential flooding of the level below. Daylights or gaps through the floor slab without sleeves are not acceptable. Refer to Division 23 — HVAC Systems for additional sleeve requirements. | Incorporated.
25 | Section 23 00 00 - HVAC Systems | Pipe Sleeves |  | Revised pipe sleeve requirements. | Incorporated.
26 | APPENDIX XXII - OLAR Requirements | Plumbing/Water |  | Mechanical spaces with water production and cagewash spaces shall be provided with a water flood alarm that is connected to the BAS, to provide alerting to a flood issue that could damage sensitive equipment such as motors and pumps. Housekeeping pads should be provided to elevate sensitive equipment in areas where flooding may occur. | Incorporated.
27 | APPENDIX XXII - OLAR Requirements | Plumbing/Water | Floor sinks will be provided in clean and dirty cage wash and will be equipped with metal covers that can be removed to facilitate ease of cleaning. | Floor sinks will be provided in clean and dirty cage wash and will be equipped with metal covers that can be removed to facilitate ease of cleaning. Metal covers must be flush with the floor level, such that rolling equipment will not be caught in grate. | Incorporated.
28 | APPENDIX XXII - OLAR Requirements | Plumbing/Water | Chemical connections and storage (for rack washer) | Chemical connections and storage (for rack washer) should be in a separate storage space, to allow delivery from the loading dock without entering the animal facility. | Incorporated.
29 | APPENDIX XXII - OLAR Requirements | Service | High pressure air needed in gnotobiotic housing areas. | High pressure air is required in gnotobiotic housing areas. | Incorporated.
30 | Section 23 00 00 - HVAC Systems | Roof Curbs |  | a. Roof curb minimum height requirements shall be as follows: 1) Rooftop penetration curb for pipes and ducts: Minimum 8-inches tall 2) Rooftop equipment curb: | Incorporated.
31 | Section 21 05 00 | Backflow Devices | Backflow Preventers — FM Global, UL, USC, ASSE, ULC, and State Fire Marshal listed and approved. a. Double check with 300 series stainless steel body and stainless steel trim. 1) Deringer Series 20 2) Deringer Series 30 3) Zurn or Wilkins #450 allowed only where the N pattern installation is required for compact fit. | Backflow Preventers — FM Global, UL, USC, ASSE, ULC, and State Fire Marshal listed and approved. a. Double check with 300 series stainless steel body and stainless steel trim. 1) Deringer Series 20 2) Deringer Series 30 3) Zurn or Wilkins #450 allowed only where the N pattern installation is required for compact fit. 4) No substitutions will be accepted. | Incorporated.

## 2026_ELECTRICAL-FIRE ALARM
SUMMARY OF PROPOSED ADDS / CHANGES - ELECTRICAL-FIRE ALARM | [6 empty] | Note: This change summary is provided for reference and highlights major revisions to the Design Guidelines. It is not intended to identify every change or requirement. The Project Team shall review the current Design Guidelines in their entirety and shall not rely solely on this summary.
ITEM # | DG SECTION # | TOPICS | CONTENT IN V5.4 | PROPOSED CONTENT | UPDATE STATUS | Comments
Column1 | Column2 | Column3 | Column4 | Column5 | Column7 | Column8
1 | 21 05 00 | Portable ABC Fire Extinguishers | Acceptable manufacturer: Amerex 5 lb. | Acceptable manufacturer: Amerex or Buckeye 5 lb. Maximum distance to nearest fire extinguisher in any lab should be no more than 50 feet. | Incorporated
2 | 26 00 00 | Third Party Tests | 5) Electrical panels shall be tested for rotation and proper phasing before their load are to be connected. 6) Electrical feeders shall be tested, as may be required by owner tested its insulation. 7) Test reports shall be provided to Caltech Electrical Engineer within 7 days of completed testing. | 5) Electrical panels shall be tested for rotation and proper phasing before their loads are to be connected. 6) Caltech standard rotation is clockwise (A, B, C) and shall be tested and mark at the building service entrance and at electrical panels. 7) Electrical feeder insulation shall be tested, as may be required by the Caltech electrical engineer. 8) Test reports shall be provided to Caltech electrical engineer within 7 days of completed testing. | Incorporated
3 | 26 05 00 | Impact Investigation |  | The contractor shall be responsible for planning, coordinating, and executing all electrical shutdowns and project impact investigations required for the work throughout the construction phase. The contractor shall coordinate investigation access and shutdown activities through the Caltech PM. The contractor shall prepare and review impact investigation findings, shutdown procedures, and outage mitigation measures with the Caltech PM and Electrical Shop prior to implementation. The contractor shall be responsible for maintaining continuity of operations and providing any required temporary or backup power necessary to support construction activities, occupied spaces, research operations, and critical systems. Costs associated with temporary or backup power shall be included as part of the project. | Incorporated
4 | 26 11 16 | Metering Section | Electro Industries Nexus 1500+ V2 or Schneider Electric METSEPM8244 power quality meter shall be installed in each designated circuit breaker that covers a building. In addition for each of the floors where applicable. The meter shall measure line currents and neutral currents, where applicable. | Electro Industries Nexus 1500+ V2 or Schneider Electric METSEPM8244 power quality meters shall be installed in each designated building’s main panel boards. The electric meters shall measure line currents and neutral currents, line-line voltages, line-neutral voltages, real power, apparent power, reactive power, current harmonics, voltage harmonics, and demand power values, where applicable. | Incorporated
5 | 26 22 00 | Low Voltage Transformers | General purpose and distribution dry type transformers shall be constructed and tested in accordance with American National Standards Institute (ANSI) and National Electric Manufacturer’s Association (NEMA) standards in addition to requirements following, and on the Drawings. They shall, without damage, withstand for two cycles the maximum fault current, which will occur with a bolted fault at the secondary terminals and with an infinite bus on the primary side. | General purpose and distribution dry type transformers shall be constructed and tested in accordance with American National Standards Institute (ANSI) and National Electric Manufacturer’s Association (NEMA) standards in addition to other requirements specified by the Caltech electrical engineer, if any. They shall, without damage, withstand for two cycles the maximum fault current, which will occur with a bolted fault at the secondary terminals and with an infinite bus on the primary side. | Incorporated
6 | 26 51 00 | Interior Lighting |  | Interior lighting shall be 3500K with a field-selectable 4000K option. Lighting fixtures longer than 4 feet, including continuous-looking runs formed by abutting fixtures together, shall be avoided unless otherwise approved by Caltech PM. Refer to Electrical Standard Lighting Specs List for Caltech preferred lighting fixtures. Obtain approval from Caltech PM and Electrical Shop for any fixtures not included on the list. Lamps should be 3500K with field-selectable 4000K option and highest available CRI. Where existing adjacent spaces utilize different color temperature, coordinate with Caltech PM, Electrical Shop and the University Architect on color selection. | Incorporated
7 | 26 51 00 | Lighting Control |  | nLight Eclypse: Where an existing space is renovated, resulting in updating the majority of a building's floor (i.e. >50%), an nLight Eclypse will be installed and networked to the scoped renovated space as completion of lighting and lighting controls scope. | Incorporated
8 | 26 56 00 | Exterior (Site) Lighting | b. Outdoor lighting poles should be the BEGA specific bronze; no other products will be accepted. Pole P/N: 14RHTS1 Pole top luminary. This part number depends on the architect lighting pattern requirements. Symmetric wide beam: PN: 84403; 4000K Asymmetric: PN: 84401; 4000K | b. Provide exterior LED lighting with 3000K CCT and highest CRI available, CRI 80% at minimum. The 3000k standard is intended to provide a warm, comfortable nighttime environment, reduce short-wavelength (blue) light associated with sky glow, limit visual glare and light pollution, and support night sky preservation while maintaining appropriate safe visibility for the campus community. c. Outdoor lighting poles should be the BEGA specific bronze; no other products will be accepted. 1) Pole P/N: 14RHTS1 2) Pole top luminary. This part number depends on the architect lighting pattern requirements. a. Symmetric wide beam: PN: 84403; 3000K b. Asymmetric: PN: 84401; 3000K | Incorporated
9 | 28 46 00 | Smoke Detectors | Smoke detectors shall be Mircom #MIX-2251B with a #MIX-B210LP mounting base. | Smoke detectors shall be Mircom #MX-2351AP with a #B300-6 mounting base. | Incorporated
10 | APPENDIX XXII | OLAR Lighting | Recess mounted, digital, battery backup 120 V light timers will be used to provide light cycles in the animal housing rooms. Digital (Intermatic ET170 series electronic 7 day timer or Tork ET 103C) light timers are preferred. | Recess mounted, digital, battery backup 120 V light timers will be used to provide light cycles in the animal holdusing and behavior testing rooms. Digital (Intermatic ET170 series electronic 7 day timer or Tork ET 103C) light timers are preferred. Some rodent holding areas may require a light timer that provides dawn/dusk light transition. OLAR will provide confirmation of lighting requirements for the species to be housed. | Incorporated

## 2026_CONTROL
SUMMARY OF PROPOSED ADDS / CHANGES - CONTROL | [6 empty] | Note: This change summary is provided for reference and highlights major revisions to the Design Guidelines. It is not intended to identify every change or requirement. The Project Team shall review the current Design Guidelines in their entirety and shall not rely solely on this summary.
ITEM # | DG SECTION # | TOPICS | CONTENT IN V5.4 | PROPOSED CONTENT | UPDATE STATUS | Comments
Column1 | Column2 | Column3 | Column4 | Column5 | Column7 | Column8
1 | 14 20 01 | Elevator Controls | 10) Control Systems: Caltech standard control system is Motion Control Engineering. a)Traction IMC or iBox AC flux vector drive. b)Hydraulic 2000 with SCR soft starter. c)Group supervisory M-3 with three or more cars. | 10) Control Systems: Caltech standard control system is Motion Control Engineering. a)Traction: iControl with AC flux vector drive. b)Hydraulic: HMC-2000 with SCR soft starter. c)Provide group operation for three or more cars. | Incorporated
2 | 23 09 00 | Enclosures Plus Contents | Enclosure located outdoors and in mechanical rooms: Waterproof rated for operation at 40 to 150°F. (NEMA 3R) | Enclosure located outdoors and in mechanical rooms: Waterproof rated for operation at 20 to 150°F. (NEMA 3R) | Incorporated
3 | 23 09 00 | Alarm Console | Refer to I/O Points Naming Convention Table for alarm class and descriptions. Alarms must conform to Caltech Niagara 4 Alarms Standards (standards to be furnished by Caltech DDC shop). | Refer to BMS Naming Standards Revision 2.0 for alarm class and descriptions. Alarms must conform to Caltech Niagara 4 Alarms Standards (standards to be furnished by Caltech DDC shop). | Incorporated
4 | 23 09 00 | Oxygen Depletion Sensor and Transmitter | Single detectors using solid-state zircon cell sensing; suitable over a temperature range of minus 32 to plus 1100°F and calibrated for 0 to 25%, with continuous or averaged reading, 4–20 mA output; for wall mounting. Sensor shall be calibration-free for 10 years. | Single detectors using solid-state zircon cell sensing; suitable over a temperature range of minus 32 to plus 110°F and calibrated for 0 to 25%, with continuous or averaged reading, 4–20 mA output; for wall mounting. Sensor shall be calibration-free for 10 years. | Incorporated
5 | 23 09 00 | Jace Controller | Tridium (JACE framework software) VYKON (JACE 8000 Series device) | Tridium (Niagara framework software) VYKON (JACE 9000 Series device) | Incorporated
6 | 23 09 00 | Jace Controller | Network Managers (JACE): (VYKON JACE 8000/9000 Series) | Network Managers (JACE): (VYKON JACE 9000 Series) | Incorporated
7 | 23 09 00 | Electronic Sensors | c) Averaging Elements in Ducts: flexible; use where prone to temperature stratification or where ducts are larger than 10 sq.ft. Mount averaging sensor across duct area in a “Z” pattern using mounting clips specific for averaging temperature sensor probes. The length and type of the sensing element will be determined based on the specific application. | Averaging Elements in Ducts: flexible; use where prone to temperature stratification or where ducts are greater than or equal to 9 sq.ft. Mount averaging sensor across duct area in a “Z” pattern using mounting clips specific for averaging temperature sensor probes. The length and type of the sensing element will be determined based on the specific application. | Incorporated
8 | 23 09 00 | Component | ABB (variable frequency drives) | ABB (DDC controllers and variable frequency drives) | Incorporated
9
10

## 2026_IMSS
SUMMARY OF PROPOSED ADDS / CHANGES - IMSS | [6 empty] | Note: This change summary is provided for reference and highlights major revisions to the Design Guidelines. It is not intended to identify every change or requirement. The Project Team shall review the current Design Guidelines in their entirety and shall not rely solely on this summary.
ITEM # | DG SECTION # | TOPICS | CONTENT IN V5.4 | PROPOSED CONTENT | UPDATE STATUS | Comments
Column1 | Column2 | Column3 | Column4 | Column5 | Column7 | Column8
1 | 27 20 00 | Voice and Data Communications |  | Maximize data capacity and reduce risk of campus network outages with future capacity needs in mind | Incorporated
2 | 27 20 00 | Voice and Data Communications |  | Clarify specs to reduce punch list items | Incorporated
3 | 27 20 00 | Voice and Data Communications |  | Update vocabulary to match industry usage | Incorporated
4 | 27 20 00 | Voice and Data Communications |  | Update data port descriptions to match current maximized usage across campus for phone and data | Incorporated
5 | 27 20 00 | Voice and Data Communications |  | Clarify lighting location requirements for telecom spaces | Incorporated
6 | 27 20 00 | Voice and Data Communications |  | Clarify minimum rack space requirements | Incorporated
7 | 27 20 00 | Voice and Data Communications |  | Update telecom room electrical requirements to match updated electrical code, including minimum campus low voltage requirements | Incorporated
8 | 27 20 00 | Voice and Data Communications |  | Add fire stop requirement that excludes the use of spray foam | Incorporated
9 | 27 20 00 | Voice and Data Communications |  | Update outside building cable requirements to meet code mandates of preserving building fire ratings | Incorporated
10 | 27 20 00 | Voice and Data Communications |  | Clarify requirements of telecom cable pathways as implemented at Caltech | Incorporated
11 | 27 20 00 | Voice and Data Communications |  | Clarify language to ensure communication cables meet “Certified Structured Cable System” requirements | Incorporated
12 | 27 40 00 | Audio / Visual Systems |  | update AV section 27 40 00 to reflect updates to computer advancements and trends, including near-universal use of HDMI | Incorporated

## 2026_SECURITY
SUMMARY OF PROPOSED ADDS / CHANGES - SECURITY | [6 empty] | Note: This change summary is provided for reference and highlights major revisions to the Design Guidelines. It is not intended to identify every change or requirement. The Project Team shall review the current Design Guidelines in their entirety and shall not rely solely on this summary.
ITEM # | DG SECTION # | TOPICS | CONTENT IN V5.4 | PROPOSED CONTENT | UPDATE STATUS | Comments
Column1 | Column2 | Column3 | Column4 | Column5 | Column7 | Column8
1 | 28 13 00 28 23 00 |  |  | Comprehensively revised to reflect Caltech's transition from legacy access control and video surveillance platforms to the current enterprise security architecture. The previous guideline primarily identified basic equipment, wiring, and installation requirements for Honeywell Win-Pak/PRO3200 and Digital Watchdog Spectrum systems. The revised guideline establishes Honeywell ProWatch with Mercury controllers for access control and Milestone with Axis cameras for video surveillance, and defines current standards for secure communications, power, cabling, network infrastructure, wireless locking, recording/storage, camera performance, and system architecture. The revision also expands the guideline beyond equipment specifications by establishing requirements for design coordination, submittals, camera placement, labeling, testing and commissioning, as-built documentation, training, and final acceptance. Access Control and Video Surveillance have been separated into dedicated sections because each system has become a distinct enterprise technology with its own design, installation, and lifecycle requirements. We removed legacy categories and equipment that are no longer part of the campus standard rather than carrying them forward where they no longer serve the current architecture. The overall intent is to give designers and contractors a clearer, more consistent campus standard while improving interoperability, maintainability, cybersecurity, scalability, and long-term support for Caltech's physical security infrastructure. | Incorporated
2
3
4
5
6
7
8
9
10